## Overview
Data Standardization in Health Care Facility Management
This file contains the draft categorization schemas for five data sets used in health care facility management.
It is meant for use by health care planners, designers, and facility operators.
Categorization schemas aligned with the FGI 2018 Guidelines for Design and Construction of Hospitals
1) Categorization of Buildings
2) Categorization of Functional Areas
3) Categorization of Spaces
These three classification schemas are draft versions that have been submitted for consideration to the Steering Committee of the FGI Health Guidelines Revision Committee (HGRC). A final version will be published in 2021 once the review of the Steering Committee is complete.
Categorization schemas aligned with UniFormat©, adjusted by ASHE for health care facility engineering
4) Categorization of Building Systems
5) Categorization of Assets
6) Diagrammatic Representation of Building Systems and Assets
These classification schemas are draft versions that have been submitted for consideration to the Operational Excellence Committee of ASHE. A final version will be published in 2021 once the review of the Operational Excellence Committee is complete.
For context, read the article "Quantifying excellence for health care facilities" in the October 2020 edition of the Health Facilities Management magazine.
https://www.hfmmagazine.com/articles/4032-quantifying-excellence-for-health-care-facilities

## Definitions
Data Standardization in Health Care Facility Management
Definitions
| Building | A discrete physical entity composed of building systems and functional areas
| Functional Area | A collection of spaces in a unit or interrelated units with persons and equipment that serve common goals
| Spaces | Either a room enclosed with walls or an area within a room with its own space identifier, such as a patient bay, cubicle, or workstation
| Building System | A grouping of one or more assets that work in unison to perform a specific function. A system may consist of mechanical equipment or structural building elements. Systems are operationally distinct from each other.
| Asset | A distinct element or an assembly of elements within a building system that requires the documentation of inspection, testing, and/or maintenance activities. Notes 1. An asset can be shared by more than one system. 2. The use of "asset" in this document aligns with the Joint Commission term "Operating Component" as used in EC.02.05.01 or EC.02.05.05.
| Sub-asset | A component of an asset. Examples of a sub-asset include a fan, motor, or a cooling/heating coil.
| Part | A consumable item for an asset, such as a belt, filter, control device, etc.

## Use Cases
Data Standardization in Health Care Facility Management
Use Cases
The five classification schemas are designed to support the following use cases.
Buildings
—Health care service location portfolio management Market analysis, lease optimization, service delivery optimization
—Energy benchmarking Using tools such as EPA Portfolio Manager or ASHE Energy-to-Care
—Operational benchmarking Operating/capital cost/GSF, FTG/GSF, patient volume/GSF
Functional Areas
—Risk management (new construction – NFPA 99; operational risk management Joint Commission EC.02.05.01)
—Risk management (operations and maintenance)
—Operational cost (maintenance intensity and energy management)
Spaces
For project planning and design per FGI Guidelines:
1.2-2.1.3 Nomenclature in the Functional Program
1.2-2.1.3.1 The names for spaces and departments used in the functional program shall be consistent with those used in the Guidelines for Design and Construction of Hospitals. If acronyms are used, they shall be clearly defined.
1.2-2.1.3.2 The names and spaces indicated in the functional program also shall be consistent with those used on submitted floor plans.
1.2-3 Space Program
A space program shall be provided that contains a list organized by department or other functional unit that shows each room in the proposed project, indicating its size by gross floor area and clear floor area and citing relevant paragraph number(s) from this document.
For facility management:
Classification of rooms in space management software to support space management function
Building Systems
—Risk management (new construction – NFPA 99; operational risk management, Joint Commission EC.02.05.01)
—Risk management (operations and maintenance)
—Assessment of system conditions, resiliency, and redundancy
—Tracking of service vendor contracts
Assets
—Supporting inspection, testing, and maintenance programs
—Alignment with documentation requirements set by regulatory agencies
—Asset-level risk management
—Asset-level reliability management

## Versions
Data Standardization in Health Care Facility Management
Versions
Categorization of Buildings
Categorization of Functional Areas
Categorization of Spaces
Version | Date | Released by | Advised by | Description
0.9 | 2020-11-20 | M. Ebinger / D. Anderson / M. Evans / D. Ford / J. Johnson / J. Guarnera | D. Erickson / P. Blumgart | Final draft, released for consideration by the Steering Committee of the FGI Health Guidelines Revision Committee (HGRC)
0.91 | 2021-01-18 | D.Anderson/M.Ebinger | D. Erickson / P. Blumgart | Addition of space category abbreviations
Categorization of Building Systems
Categorization of Assets
Diagrammatic Representation of Assets and Systems
Version | Date | Released by | Advised by | Description
0.9 | 2020-11-20 | F. Rudilosso / J. Zepp / J. Johnson / G. Oberlander / R. Schramm / M. Ebinger | J. Flannery | Final draft, released for consideration by the Operational Excellence Committee of the American Society for Health Care Engineering (ASHE)

## Acknowledgments
Data Standardization in Health Care Facility Management
Acknowledgments
We appreciate the tremendous work of all who participated in the development of these classification standards during a turbulent 2020.
Thank you for your effort in developing a foundation that will transform facility management in the health care industry.
Health Care Facility Data Standardization (HFDS) working group - Steering Committee
The HFDS is an unaffiliated ad-hoc working group that incubated the development of these standards. The working group is expected to dissolve as these standards merge into the formal structures established by ASHE and FGI.
Carbery, Stephen - YNHH
Ceton, Greg - CSI
Ebinger, Matthias - Enstoa
Erickson, Douglas - FGI
Evans, Michele - NIH
Flannery, Jonathan - ASHE
Ford, Dennis - Atrium Health
Friedman, Steven - MSKCC
Johnson, Johnathan - NIH
Maggio, Charles - CBRE
Poulos, John - CBRE
Rudilosso, Frank - NYP
FGI Nomenclature Topic Group
This topic group developed the draft classifications for buildings, functional areas, and spaces during the spring, summer, and early fall of 2020. The topic group is submitting its proposed nomenclature classification to the FGI Steering Committee of the Health Guidelines Revision Committee (HGRC) for consideration for the 2022 Guidelines edition.
Anderson, Donna-Lee - YNHH (Co-Chair)
Andersson, Lennart - FormD NY
Blumgart, Pamela - FGI (Adviser)
Ceton, Greg - CSI
Dalton, Ellie - NYP
Ebinger, Matthias - Enstoa (Chair)
Erickson, Douglas - FGI (Adviser)
Evans, Michele - NIH (Liaison to FGI HGRC)
Flannery, Jonathan - (Adviser)
Ford, Dennis - Atrium Health (Co-Chair)
Guarnera, Jessica - CBRE
Johnson, Johnathan - NIH
Krieger, Liesl - CBRE
Oberlander, George - CFS Facilities Management
O'Brien, John - SSM Health
Poulos, John - CBRE
Rudilosso, Frank - NYP
Schramm, Ryan - M Health Fairview
Stockman, Joe - Facilities Survey
Van der Linden, Girlie - NYP
Asset Classification Working Group
This working group developed the draft classifications for building systems and assets during the spring and summer of 2020 for review by the ASHE Operational Excellence Committee.This working group will continue as a working group of the ASHE Operational Excellence Committee. Contact the chair if you are interested in joining.
Camacho, Kristin - CFS
Ebinger, Matthias - Enstoa
Flannery, Jonathan - ASHE (Advisor)
Johnson, Johnathan - NIH
Oberlander, George - CFS
Palmer, Charles - Enstoa
Rudilosso, Frank - NYP (Chair)
Schramm, Ryan - M Health Fairview
Zepp, John - CFS

## 1) Buildings
Data Standardization in Health Care Facility Management | Source: | FGI Facility Types | https://fgiguidelines.org/guidelines/2018-fgi-guidelines/
Categorization of Buildings |  | EPA Portfolio Manager | https://www.energystar.gov/buildings/tools-and-resources/list-portfolio-manager-property-types-definitions-and-use-details
Version 0.9 | Notes: | 1. Since health care organizations often manage a larger portfolio of buildings, this tab includes all EPA Property Types, not just Property Types for health care.
2. The FGI facility types included in this table come from the 2018 FGI Guidelines document for hospitals; outpatient facilities; and residential health and care facilities.
3. To measure building gross square footage (BGSF), use of the process provided in the 2017 ASHE Monograph “Area Calculation Method for Health Care” is recommended (https://www.ashe.org/areacalculation)
FGI Facility Type | EPA Portfolio Manager Property Types |  |  | EPA Property Types, expanded with FGI Facility Types
FGI Facility Type | EPA Property Types Level 1 | EPA Property Types Level 2 | EPA Property Types Level 3 | Proposed Healthcare Building Portfolio Lookup | Also known as:
H-2.2 General Hospital | Healthcare | Hospital |  | Healthcare - Hospital
H-2.3/OP 2.8 Freestanding Emergency Care Facility | Healthcare | Hospital |  | Healthcare - Hospital - Freestanding Emergency Care
H-2.4 Critical Access Hospital | Healthcare | Hospital |  | Healthcare - Hospital - Critical Access Hospital
H-2.5 Psychiatric Hospital | Healthcare | Specialty Hospital |  | Healthcare - Hospital - Psychiatric Hospital
H-2.6 Rehabilitation Hospital | Healthcare | Specialty Hospital |  | Healthcare - Hospital - Rehabilitation Hospital
H-2.7 Children's Hospital | Healthcare | Hospital |  | Healthcare - Hospital - Children's Hospital
OP-2.2 General and Specialty Medical Services Facilities
OP-2.2 Community-based clinic | Healthcare | Urgent Care/Clinic/Other Outpatient |  | Healthcare - Outpatient - Community-Based Clinic
OP-2.2 Micro-clinic | Healthcare | Urgent Care/Clinic/Other Outpatient |  | Healthcare - Outpatient - Micro-Clinic
OP-2.2 Multi-specialty medical clinic/office building | Healthcare | Medical Office |  | Healthcare - Medical Office - Multi-Specialty
OP-2.2 Neighborhood clinic | Healthcare | Urgent Care/Clinic/Other Outpatient |  | Healthcare - Outpatient - Neighborhood Clinic
OP-2.2 Physician practice | Healthcare | Medical Office |  | Healthcare - Medical Office - Physician Practice
OP-2.2 Primary care center | Healthcare | Medical Office |  | Healthcare - Medical Office - Primary Care Center
OP-2.2 Retail clinic | Healthcare | Urgent Care/Clinic/Other Outpatient |  | Healthcare - Outpatient - Retail Clinic
OP-2.2 Single-specialty medical clinic/office building | Healthcare | Medical Office |  | Healthcare - Medical Office - Single-Specialty Medical
OP-2.2 Sole practitioner clinic | Healthcare | Urgent Care/Clinic/Other Outpatient |  | Healthcare - Outpatient - Sole Practitioner Clinic
OP-2.3 Outpatient Imaging Facility | Healthcare | Medical Office |  | Healthcare - Medical Office - Imaging Facility
OP-2.4 Birth Center | Healthcare | Urgent Care/Clinic/Other Outpatient |  | Healthcare - Outpatient - Birth Center
OP-2.5 Urgent Care Center | Healthcare | Urgent Care/Clinic/Other Outpatient |  | Healthcare - Outpatient - Urgent Care Center
OP-2.6 Infusion Center | Healthcare | Medical Office |  | Healthcare - Medical Office - Infusion Center
OP-2.7 Outpatient Surgery Facility | Healthcare | Ambulatory Surgical Center |  | Healthcare - Outpatient - Surgery Facility
OP-2.9 Endoscopy Facility | Healthcare | Medical Office |  | Healthcare - Medical Office - Endoscopy Facility
OP-2.10 Renal Dialysis Center | Healthcare | Medical Office |  | Healthcare - Medical Office - Renal Dialysis Center
OP-2.11 Outpatient Psychiatric Center | Healthcare | Medical Office |  | Healthcare - Medical Office - Psychiatric Center
OP-2.12 Outpatient Rehabilitation Therapy Facility | Healthcare | Outpatient Rehabilitation/Physical Therapy |  | Healthcare - Outpatient - Rehabilitation Therapy Facility
OP-2.14 Dental Facility | Healthcare | Medical Office |  | Healthcare - Outpatient - Dental Facility
R-3.1 Nursing Home | Healthcare | Residential Care Facility or Senior Care Facility |  | Healthcare - Residential Care - Nursing Home | - Convalescent Home - Long-Term Care - Rest Homes - Retirement Home - Memory Care Center - Dementia Care Center - Skilled Nursing Home
R-3.2 Hospice Facility | Healthcare | Residential Care Facility or Senior Care Facility |  | Healthcare - Residential Care - Hospice Facility | - End-of-Life Care - Hospice House - Elder Hostel - Hospice Care - Convalescent Home - Rest Homes
R-4.1 Assisted Living Facility | Healthcare | Residential Care Facility or Senior Care Facility |  | Healthcare - Residential Care - Assisted Living Facility | - Intermediate Care Facility - Retirement Community - Retirement Home - Care Facility - Senior Living Facility
R-4.2 Independent Living Settings | Lodging/ Residential | Multifamily Housing |  | Lodging/Residential - Multifamily Housing - Independent Living
R-4.3 Substance Abuse Treatment | Healthcare | Residential Care Facility |  | Healthcare - Residential Care - Substance Abuse Treatment | - Drug Treatment Facility - Alcohol and Drug Recovery Center - Drug and Alcohol Rehab Center - Chemical Dependency Treatment Center
R-4.4 Developmental Disability Care | Healthcare | Residential Care Facility |  | Healthcare - Residential Care - Developmental Disability Care | - Developmental Disability Residential Treatment Center - Residential Living for Adults with Intellectual or Developmental Disabilities - Residential Treatment Facility - Residential Intellectual Disability Facility - Residential Care for Disabled - Community-Based Residential Community
| Banking/Financial Services | Bank Branch |  | Banking/Financial Services - Bank Branch
| Banking/Financial Services | Financial Office |  | Banking/Financial Services - Financial Office
| Education | Adult Education |  | Education - Adult Education
| Education | College/University |  | Education - College/University
| Education | K-12 School |  | Education - K-12 School
| Education | Other - Education |  | Education - Other - Education
| Education | Pre-school/Daycare |  | Education - Pre-school/Daycare
| Education | Vocational School |  | Education - Vocational School
| Entertainment/Public Assembly | Convention Center |  | Entertainment/Public Assembly - Convention Center
| Entertainment/Public Assembly | Movie Theater |  | Entertainment/Public Assembly - Movie Theater
| Entertainment/Public Assembly | Museum |  | Entertainment/Public Assembly - Museum
| Entertainment/Public Assembly | Other | Aquarium | Entertainment/Public Assembly - Other - Aquarium
| Entertainment/Public Assembly | Other | Bar/Nightclub | Entertainment/Public Assembly - Other - Bar/Nightclub
| Entertainment/Public Assembly | Other | Casino | Entertainment/Public Assembly - Other - Casino
| Entertainment/Public Assembly | Other | Other - Entertainment/Public Assembly | Entertainment/Public Assembly - Other - Other - Entertainment/Public Assembly
| Entertainment/Public Assembly | Other | Zoo | Entertainment/Public Assembly - Other - Zoo
| Entertainment/Public Assembly | Performing Arts |  | Entertainment/Public Assembly - Performing Arts
| Entertainment/Public Assembly | Recreation | Bowling Alley | Entertainment/Public Assembly - Recreation - Bowling Alley
| Entertainment/Public Assembly | Recreation | Fitness Center/Health Club/Gym | Entertainment/Public Assembly - Recreation - Fitness Center/Health Club/Gym
| Entertainment/Public Assembly | Recreation | Ice/Curling Rink | Entertainment/Public Assembly - Recreation - Ice/Curling Rink
| Entertainment/Public Assembly | Recreation | Other - Recreation | Entertainment/Public Assembly - Recreation - Other - Recreation
| Entertainment/Public Assembly | Recreation | Roller Rink | Entertainment/Public Assembly - Recreation - Roller Rink
| Entertainment/Public Assembly | Recreation | Swimming Pool | Entertainment/Public Assembly - Recreation - Swimming Pool
| Entertainment/Public Assembly | Social/Meeting Hall |  | Entertainment/Public Assembly - Social/Meeting Hall
| Entertainment/Public Assembly | Stadium | Indoor Arena | Entertainment/Public Assembly - Stadium - Indoor Arena
| Entertainment/Public Assembly | Stadium | Other - Stadium | Entertainment/Public Assembly - Stadium - Other - Stadium
| Entertainment/Public Assembly | Stadium | Race Track | Entertainment/Public Assembly - Stadium - Race Track
| Entertainment/Public Assembly | Stadium | Stadium (Closed) | Entertainment/Public Assembly - Stadium - Stadium (Closed)
| Entertainment/Public Assembly | Stadium | Stadium (Open) | Entertainment/Public Assembly - Stadium - Stadium (Open)
| Food Sales & Service | Convenience Store | Convenience Store with Gas Station | Food Sales & Service - Convenience Store - Convenience Store with Gas Station
| Food Sales & Service | Convenience Store | Convenience Store without Gas Station | Food Sales & Service - Convenience Store - Convenience Store without Gas Station
| Food Sales & Service | Other | Food Sales | Food Sales & Service - Other - Food Sales
| Food Sales & Service | Other | Food Service | Food Sales & Service - Other - Food Service
| Food Sales & Service | Restaurant/Bar | Bar/Nightclub | Food Sales & Service - Restaurant/Bar - Bar/Nightclub
| Food Sales & Service | Restaurant/Bar | Fast Food Restaurant | Food Sales & Service - Restaurant/Bar - Fast Food Restaurant
| Food Sales & Service | Restaurant/Bar | Other - Restaurant/Bar | Food Sales & Service - Restaurant/Bar - Other - Restaurant/Bar
| Food Sales & Service | Restaurant/Bar | Restaurant | Food Sales & Service - Restaurant/Bar - Restaurant
| Food Sales & Service | Supermarket/Grocery Store |  | Food Sales & Service - Supermarket/Grocery Store
| Food Sales & Service | Wholesale Club/Supercenter |  | Food Sales & Service - Wholesale Club/Supercenter
| Lodging/Residential | Barracks |  | Lodging/Residential - Barracks
| Lodging/Residential | Hotel |  | Lodging/Residential - Hotel
| Lodging/Residential | Multifamily Housing |  | Lodging/Residential - Multifamily Housing
| Lodging/Residential | Other |  | Lodging/Residential - Other
| Lodging/Residential | Prison/Incarceration |  | Lodging/Residential - Prison/Incarceration
| Lodging/Residential | Residence Hall/Dormitory |  | Lodging/Residential - Residence Hall/Dormitory
| Lodging/Residential | Residential Care Facility |  | Lodging/Residential - Residential Care Facility
| Lodging/Residential | Senior Care Community |  | Lodging/Residential - Senior Care Community
| Lodging/Residential | Single Family Home |  | Lodging/Residential - Single Family Home
| Manufacturing/Industrial | Manufacturing/Industrial Plant |  | Manufacturing/Industrial - Manufacturing/Industrial Plant
| Mixed Use | Mixed Use Property |  | Mixed Use - Mixed Use Property
| Office | Office |  | Office - Office
| Office | Veterinary Office |  | Office - Veterinary Office
| Other | Other |  | Other - Other
| Parking | Parking |  | Parking - Parking
| Public Services | Courthouse |  | Public Services - Courthouse
| Public Services | Drinking Water Treatment & Distribution |  | Public Services - Drinking Water Treatment & Distribution
| Public Services | Fire Station |  | Public Services - Fire Station
| Public Services | Library |  | Public Services - Library
| Public Services | Mailing Center/Post Office |  | Public Services - Mailing Center/Post Office
| Public Services | Other |  | Public Services - Other
| Public Services | Police Station |  | Public Services - Police Station
| Public Services | Prison/Incarceration |  | Public Services - Prison/Incarceration
| Public Services | Social/Meeting Hall |  | Public Services - Social/Meeting Hall
| Public Services | Transportation Terminal/Station |  | Public Services - Transportation Terminal/Station
| Public Services | Wastewater Treatment Plant |  | Public Services - Wastewater Treatment Plant
| Religious Worship | Worship Facility |  | Religious Worship - Worship Facility
| Retail | Automobile Dealership |  | Retail - Automobile Dealership
| Retail | Convenience Store | Convenience Store with Gas Station | Retail - Convenience Store - Convenience Store with Gas Station
| Retail | Convenience Store | Convenience Store without Gas Station | Retail - Convenience Store - Convenience Store without Gas Station
| Retail | Mall | Enclosed Mall | Retail - Mall - Enclosed Mall
| Retail | Mall | Lifestyle Center | Retail - Mall - Lifestyle Center
| Retail | Mall | Other - Mall | Retail - Mall - Other - Mall
| Retail | Mall | Strip Mall | Retail - Mall - Strip Mall
| Retail | Retail Store |  | Retail - Retail Store
| Retail | Supermarket/Grocery Store |  | Retail - Supermarket/Grocery Store
| Retail | Wholesale Club/Supercenter |  | Retail - Wholesale Club/Supercenter
| Services | Data Center |  | Services - Data Center
| Services | Other |  | Services - Other
| Services | Personal Services (Health/Beauty, Dry Cleaning, etc.) |  | Services - Personal Services (Health/Beauty, Dry Cleaning, etc.)
| Services | Repair Services (Vehicle, Shoe, Locksmith, etc.) |  | Services - Repair Services (Vehicle, Shoe, Locksmith, etc.)
| Technology/Science | Data Center |  | Technology/Science - Data Center
| Technology/Science | Laboratory |  | Technology/Science - Laboratory
| Technology/Science | Other |  | Technology/Science - Other
| Utility | Drinking Water Treatment & Distribution |  | Utility - Drinking Water Treatment & Distribution
| Utility | Energy/Power Station |  | Utility - Energy/Power Station
| Utility | Other |  | Utility - Other
| Utility | Wastewater Treatment Plant |  | Utility - Wastewater Treatment Plant
| Warehouse/Storage | Self-Storage Facility |  | Warehouse/Storage - Self-Storage Facility
| Warehouse/Storage | Warehouse/Distribution Center | Distribution Center | Warehouse/Storage - Warehouse/Distribution Center - Distribution Center
| Warehouse/Storage | Warehouse/Distribution Center | Non-Refrigerated Warehouse | Warehouse/Storage - Warehouse/Distribution Center - Non-Refrigerated Warehouse
| Warehouse/Storage | Warehouse/Distribution Center | Refrigerated Warehouse | Warehouse/Storage - Warehouse/Distribution Center - Refrigerated Warehouse

## 2) Functional Areas
Data Standardization in Health Care Facility Management | Source: | FGI Facility Types | https://fgiguidelines.org/guidelines/2018-fgi-guidelines/
Categorization of Functional Areas | Notes: | See notes below the table.
Version 0.9
Department or Other Functional Area | FGI Reference
Building Support ¦ Engineering and Maintenance Services | 2.1-5.6
Building Support ¦ Environmental Services | 2.1-5.5
Building Support ¦ Materials Management | 2.1-5.3
Building Support ¦ Waste Management | 2.1-5.4
Clinical Service ¦ Laboratory Services | 2.1-4.1
Clinical Service ¦ Pharmacy Services | 2.1-4.2
Clinical Support ¦ Linen Services | 2.1-5.2
Clinical Support ¦ Morgue Services | 2.1-5.7
Clinical Support ¦ Sterile Processing | 2.1-5.1
D&T ¦ Electroconvulsive Therapy | 2.5-3.4
D&T ¦ Emergency Services | 2.2-3.1
D&T ¦ Endoscopy Services | 2.2-3.11
D&T ¦ Hyperbaric Suite | 2.2-3.13
D&T ¦ Imaging Services | 2.2-3.4
D&T ¦ Infusion Therapy | 2.2-3.12
D&T ¦ Intensive Outpatient and Partial Hospitalization Program | 2.2-3.14 (2022 Guidelines)
D&T ¦ Observation Unit | 2.2-3.2
D&T ¦ Pre- and Post-Procedure Patient Care Areas | 2.1-3.4
D&T ¦ Radiation Therapy | 2.2-3.5
D&T ¦ Rehabilitation Therapy | 2.6-3.1
D&T ¦ Renal Dialysis Services | 2.2-3.10
D&T ¦ Respiratory Therapy | 2.2-3.9
D&T ¦ Surgical Services | 2.2-3.3
D&T ¦ Telemedicine Services | 2.1-3.3
Food and Nutrition Services | 2.1-4.3
Patient Care ¦ Alzheimer’s and Other Dementia Patient Care Unit | 2.5-2.4
Patient Care ¦ Bariatric Patient Care Unit | 2.2-2.14
Patient Care ¦ Behavioral and Mental Health Patient Care Unit – Forensic | 2.5-2.5
Patient Care ¦ Behavioral and Mental Health Patient Care Unit – General | 2.5-2.2
Patient Care ¦ Behavioral Health Crisis Unit | 2.2-2.17 (2022 Guidelines)
Patient Care ¦ Burn Trauma Intensive Care Unit | 2.2-2.16 (2022 Guidelines)
Patient Care ¦ Critical Access Patient Care Unit | 2.4-2.2
Patient Care ¦ Hospice Patient Care Unit | 2.2-2.15
Patient Care ¦ In-Hospital Skilled Nursing Patient Care Unit | 2.2-2.13
Patient Care ¦ Intensive Care Unit | 2.2-2.6
Patient Care ¦ Intermediate Care Unit | 2.2-2.5
Patient Care ¦ Medical/Surgical Patient Care Unit | 2.2-2.2
Patient Care ¦ Neonatal Intensive Care Unit | 2.2-2.8
Patient Care ¦ Nursery Unit | 2.2-2.10
Patient Care ¦ Obstetrical Unit | 2.2-2.9
Patient Care ¦ Oncology Patient Care Unit | 2.2-2.3
Patient Care ¦ Patient Living Areas | 2.6-2.3
Patient Care ¦ Pediatric and Adolescent Oncology Patient Care Unit | 2.2-2.4
Patient Care ¦ Pediatric and Adolescent Patient Care Unit | 2.2-2.11
Patient Care ¦ Pediatric Behavioral and Mental Health Patient Care Unit | 2.5-2.3
Patient Care ¦ Pediatric Intensive Care Unit | 2.2-2.7
Patient Care ¦ Pediatric Medical/Surgical Patient Care Unit | 2.7-2.2
Patient Care ¦ Rehabilitation Patient Care Unit | 2.6-2.2
Public and Administrative Areas ¦ Administrative Areas | 2.1-6.3
Public and Administrative Areas ¦ Public Areas | 2.1-6.2
Public and Administrative Areas ¦ Structured Parking | Not covered in FGI
Public and Administrative Areas ¦ Surface Parking | Not covered in FGI
Notes
1. This table includes some functional areas not covered in the FGI Guidelines. The added functional areas cover commonly expected areas in hospitals and are included here so this classification schema can be used “as is” to support functional programming or space benchmarking. 2. FGI citations are from the 2018 Hospital Guidelines; however, some hospital functional area and space types may apply to functional areas and spaces in some outpatient facility types. This table does not include functional areas from the 2018 Residential Guidelines. 3. D&T stands for "diagnostic and treatment." 4. To measure the square footage for functional areas, use of the definition for “departmental gross square footage” (DGSF) as provided in the 2017 ASHE monograph “Area Calculation Method for Health Care” is recommended (https://www.ashe.org/areacalculation).

## 3) Spaces
Data Standardization in Health Care Facilities Management |  | Source: |  | FGI Facility Types | https://fgiguidelines.org/guidelines/2018-fgi-guidelines/
Categorization of Spaces |  | Notes: |  | See notes below the table.
Version 0.91
Grouping | Space Name | Abbreviation | Long Version | 2018 FGI Hospital Reference | Comments | ASHRAE 170 Addendum P
Building Support | Central Waste Collection and Storage | STRG-WASTE-CTR | Central Waste Collection and Storage [STRG-WASTE-CTR] | 2.1-5.4.1
Building Support | Chute Discharge - Soiled Linen | CHUTE-LINEN | Chute Discharge - Soiled Linen [CHUTE-LINEN] | 2.1-5.4.1.4 | Linen and trash chute rom, see also to 2.1-5.2.2.1 (1)(b) | Linen and refuse chute room
Building Support | Chute Access - Trash | CHUTE-TRASH | Chute Access - Trash [CHUTE-TRASH] | 2.1-5.4.1.4 |  | Linen and refuse chute room
Building Support | Command Center | COMMAND | Command Center [COMMAND] | Not covered in FGI
Building Support | Electrical Equipment Room/Closet | ELEC | Electrical Equipment Room/Closet [ELEC] | 2.1-5.6.2
Building Support | Electrical Vault | ELEC-VAULT | Electrical Vault [ELEC-VAULT] | 2.1-5.6.2
Building Support | Elevator Machine Room | ELEV-EQUIP | Elevator Machine Room [ELEV-EQUIP] | Not covered in FGI
Building Support | Emergency Generator Room | EMER-GEN | Emergency Generator Room [EMER-GEN] | 2.1-5.6.2
Building Support | Facility Management Office | FM-WRK | Facility Management Office [FM-WRK] | 2.1-5.6.6
Building Support | Fire Protection Equipment Room/Closet | FP-EQUIP | Fire Protection Equipment Room/Closet [FP-EQUIP] | Not covered in FGI | Rooms/closets for fire pumps, pre-action sprinklers, sprinkler valves etc.
Building Support | Hazardous Material Storage | STRG-HAZ | Hazardous Material Storage [STRG-HAZ] | 2.1-4.1.2.4, 2.1-5.4.1 |  | Hazardous material storage
Building Support | Interstitial Space | INTERSTITIAL | Interstitial Space [INTERSTITIAL] | Not covered in FGI
Building Support | Materials Management, Central Storage | STRG-CTRL-MM | Materials Management, Central Storage [STRG-CTRL-MM] | 2.1-5.3.3
Building Support | Materials Management, Emergency Stock | STRG-EMER-MM | Materials Management, Emergency Stock [STRG-EMER-MM] | A2.1-5.3.3.1-a
Building Support | Materials Management, Loading Dock | DOCK | Materials Management, Loading Dock [DOCK] | 2.1-5.3.2.1
Building Support | Materials Management, Receiving Area | RECV | Materials Management, Receiving Area [RECV] | 2.1-5.3.2.2 | Includes staging areas
Building Support | Mechanical Equipment Room/Closet | MECH | Mechanical Equipment Room/Closet [MECH] | 2.1-5.6.2
Building Support | Medical Gas Cylinder Storage Room | STRG-MEDGAS | Medical Gas Cylinder Storage Room [STRG-MEDGAS] | 2.1-8.4.4
Building Support | Medical Gas Manifold Room | MEDGAS-CTRL | Medical Gas Manifold Room [MEDGAS-CTRL] | 2.1-8.4.4
Building Support | Plant, Shop | SHOP | Plant, Shop [SHOP] | 2.1-5.6.4
Building Support | Plant, Storage | STRG-PLANT | Plant, Storage [STRG-PLANT] | 2.1-5.6.3
Building Support | Plumbing Equipment Room/Closet | PLBG | Plumbing Equipment Room/Closet [PLBG] | Not covered in FGI
Building Support | Regulated Waste Holding | STRG-WASTE-HAZ | Regulated Waste Holding [STRG-WASTE-HAZ] | 2.1-5.4.1.3 |  | Regulated waste holding spaces
Building Support | Security and Alarm Equipment Room | SEC-ALARM | Security and Alarm Equipment Room [SEC-ALARM] | Not covered in FGI
Building Support | Switchgear Room | ELEC-SWITCH | Switchgear Room [ELEC-SWITCH] | 2.1-5.6.2
Building Support | Technology equipment center | TECH-EQUIP | Technology equipment center [TECH-EQUIP] | 2.1-8.5.2.2 | 2022 FGI: Technology equipment room
Building Support | Telecommunications - Technology distribution room | TDR | Telecommunications - Technology distribution room [TDR] | 2.1-8.5.2.3 | 2022 FGI: Telecommunications room
Building Support | Telecommunications entrance room | TER | Telecommunications entrance room [TER] | 2.1-8.5.2.1 | 2022 FGI: Telecommunications entrance facility or main point of entry
Building Support | Tunnel | TUNNEL | Tunnel [TUNNEL] | Not covered in FGI
Building Support | Waste Treatment and Disposal | WASTE-PRCS | Waste Treatment and Disposal [WASTE-PRCS] | 2.1-5.4.2 | In central facility area
Clinical Service | Laboratory Analysis and Manual Processing | LAB-PRCS | Laboratory Analysis and Manual Processing [LAB-PRCS] | 2.1-4.1.2.1 | “Laboratory workstations” in FGI (includes bacteriology, biochemistry, cytology, general, histology, microbiology, pathology, serology labs) | Laboratory work area
Clinical Service | Laboratory glasswashing | LAB-WASH | Laboratory glasswashing [LAB-WASH] | Not covered in FGI | Not covered explicitly in FGI but individually called out in ASHRAE 170 | Laboratory work area, glasswashing
Clinical Service | Laboratory media transfer | LAB-MED-XFR | Laboratory media transfer [LAB-MED-XFR] | Not covered in FGI | Not covered explicitly in FGI but individually called out in ASHRAE 170 | Laboratory work area, media transfer
Clinical Service | Laboratory Refrigerated Storage | STRG-LAB-REF | Laboratory Refrigerated Storage [STRG-LAB-REF] | 2.1-4.1.2.3
Clinical Service | Laboratory Specimen Collection Facilities | LAB-COLL | Laboratory Specimen Collection Facilities [LAB-COLL] | 2.1-4.1.3
Clinical Service | Laboratory Storage | STRG-LAB | Laboratory Storage [STRG-LAB] | 2.1-4.1.2.4
Clinical Service | Laboratory Terminal Sterilization | LAB-STRL | Laboratory Terminal Sterilization [LAB-STRL] | 2.1-4.1.2.6 |  | Laboratory work area, sterilizing
Clinical Service | Pharmacy Dispensing Area | PHARM-DISP | Pharmacy Dispensing Area [PHARM-DISP] | 2.1-4.2.2.1 |  | Pharmacy services: pharmacy areas
Clinical Service | Pharmacy Hazardous Drug Compounding Room | PHARM-COMP-HAZ | Pharmacy Hazardous Drug Compounding Room [PHARM-COMP-HAZ] | 2.1-4.2.2.2
Clinical Service | Pharmacy Hazardous Drug IV Preparation Room | PHARM-IV-HAZ | Pharmacy Hazardous Drug IV Preparation Room [PHARM-IV-HAZ] | 2.1-4.2.3.3
Clinical Service | Pharmacy IV Preparation Area | PHARM-IV | Pharmacy IV Preparation Area [PHARM-IV] | 2.1-4.2.3.2
Clinical Service | Pharmacy Non-Hazardous Drug Compounding Room | PHARM-COMP | Pharmacy Non-Hazardous Drug Compounding Room [PHARM-COMP] | 2.1-4.2.2.2
Clinical Service | Pharmacy Sterile Work Area | PHARM-STRL | Pharmacy Sterile Work Area [PHARM-STRL] | 2.1-4.2.3 |  | Pharmacy services: pharmacy areas
Clinical Service | Pharmacy Storage | STRG-PHARM | Pharmacy Storage [STRG-PHARM] | 2.1-4.2.2.3 |  | Pharmacy services: pharmacy areas
Clinical Service | Radiopharmaceutical Production Pharmacy | PHARM-HOT | Radiopharmaceutical Production Pharmacy [PHARM-HOT] | 2.2-3.4.8.21
Clinical Service | Support Areas for the Laboratory | LAB-SUPT | Support Areas for the Laboratory [LAB-SUPT] | 2.1-4.1.8
Clinical Support | Admissions Area | ADMIT | Admissions Area [ADMIT] | 2.1-6.3.1
Clinical Support | Anesthesia Workroom | ANES-WRK | Anesthesia Workroom [ANES-WRK] | 2.2-3.3.3
Clinical Support | Anteroom | ANTE | Anteroom [ANTE] | 2.1-2.4.2.3 | FGI reference is for AII anterooms
Clinical Support | Autopsy Room | AUTOPSY | Autopsy Room [AUTOPSY] | 2.1-5.7.2.2 |  | Autopsy room
Clinical Support | Body-Holding Area, Refrigerated | BODY-HOLD-REF | Body-Holding Area, Refrigerated [BODY-HOLD-REF] | 2.1-5.7.2.1
Clinical Support | Body-Holding Room, Non-Refrigerated | BODY-HOLD | Body-Holding Room, Non-Refrigerated [BODY-HOLD] | 2.1-5.7.3 |  | Non-refrigerated body-holding room
Clinical Support | Central Storage Clean Linen | STRG-LINEN-CTR | Central Storage Clean Linen [STRG-LINEN-CTR] | 2.1-5.2.2.1 (3) | General support area, also see 2.8.13.1 | Clean linen storage room
Clinical Support | Chute Access - Soiled Linen | CHUTE-LINEN | Chute Access - Soiled Linen [CHUTE-LINEN] | 2.1-5.2.2.1 (1)(b) | Linen and trash chute room, see also 2.1-5.4.1.4 | Linen and refuse chute room
Clinical Support | Clean Scope Storage | STRG-SCOPE | Clean Scope Storage [STRG-SCOPE] | 2.2-3.11.4.3 (4) |  | Sterile storage room
Clinical Support | Clean Supply Room | STRG-CLN | Clean Supply Room [STRG-CLN] | 2.1-2.8.11.3 |  | Clean supply room
Clinical Support | Clean Workroom | CLN-WRK | Clean Workroom [CLN-WRK] | 2.1-2.8.11.2 |  | Clean workroom
Clinical Support | Control Room or Alcove | CTRL | Control Room or Alcove [CTRL] | 2.2-3.3.4.3, 2.2-3.4.1.3 (1) | Not exclusively imaging (although FGI references are imaging only)
Clinical Support | Control Station | CTRL-STN | Control Station [CTRL-STN] | 2.2-3.1.2.3 (ED) 2.2-3.3.6.2 (Surgery) 2.2-3.4.8.2 (Imaging) | Access to surgery, imaging suite
Clinical Support | Cyclotron Room | CYCLOTRON | Cyclotron Room [CYCLOTRON] | 2.2-3.4.7.3 (4)
Clinical Support | Decentralized Sterile Processing | SP-DECNTRLZD | Decentralized Sterile Processing [SP-DECNTRLZD] | 2.1-5.1.2.2, 2.1-5.1.2.3, 2.2-3.3.6.15 | One- or two-room sterile processing facility in the restricted area of the surgical suite | Decontamination room, clean workroom (if two-room sterile processing facility
Clinical Support | Dialysis Water Treatment Equipment Room | DLYS-WATER-EQUIP | Dialysis Water Treatment Equipment Room [DLYS-WATER-EQUIP] | 2.2-3.10.8.18
Clinical Support | Documentation Area | DOCUM | Documentation Area [DOCUM] | 2.1-2.8.3
Clinical Support | ED Entrance | ED-ENTRY | ED Entrance [ED-ENTRY] | 2.2-3.1.3.2
Clinical Support | ED Public Waiting Area | ED-WAIT | ED Public Waiting Area [ED-WAIT] | 2.2-3.1.3.4 |  | ED public waiting area
Clinical Support | EMS Communications | EMS-COMM | EMS Communications [EMS-COMM] | 2.2-3.1.3.5
Clinical Support | EMS Station | EMS-STN | EMS Station [EMS-STN] | 2.2-3.1.3.6 | Base station, documentation station
Clinical Support | Endoscope Clean Work Area | ENDO-CLN | Endoscope Clean Work Area [ENDO-CLN] | 2.2-3.11.4.3 |  | Clean workroom
Clinical Support | Endoscope Decontamination Area | ENDO-DECON | Endoscope Decontamination Area [ENDO-DECON] | 2.2-3.11.4.2 | Endoscope cleaning | Endoscope cleaning
Clinical Support | Endoscope Processing Room | ENDO-PRCS | Endoscope Processing Room [ENDO-PRCS] | 2.2-3.11.4 | Used when the decon and clean areas are not separate rooms | Endoscope cleaning
Clinical Support | Environmental Services (EVS) Room | EVS | Environmental Services (EVS) Room [EVS] | 2.1-2.8.14 |  | EVS room
Clinical Support | Equipment Storage | STRG-EQUIP | Equipment Storage [STRG-EQUIP] | 2.1-2.8.13.2
Clinical Support | EVS Cart Cleaning | CART-CLN | EVS Cart Cleaning [CART-CLN] | 2.1-5.5.2 | Serves central services department, food and nutrition facilities, and linen services; Differs from Sterile Processing Department cart wash
Clinical Support | Frozen Section Prep and Exam | FRZ-PREP | Frozen Section Prep and Exam [FRZ-PREP] | 2.2-3.3.8.17
Clinical Support | Health Information Management (HIM) | HIM | Health Information Management (HIM) [HIM] | 2.1-6.3.5 | FGI: Medical Records Area
Clinical Support | Heliport | HPORT | Heliport [HPORT] | 1.3-3.7.1
Clinical Support | HIM Records Pickup | HIM-PUB | HIM Records Pickup [HIM-PUB] | Not covered in FGI | Where patients interact with staff to retrieve non-digital records
Clinical Support | Imaging Contrast Media Prep Area | MEDIA-PREP | Imaging Contrast Media Prep Area [MEDIA-PREP] | 2.2-3.4.8.16
Clinical Support | Imaging Interpretation/Reading Room | READ | Imaging Interpretation/Reading Room [READ] | 2.2-3.4.8.18
Clinical Support | Infant Feeding Preparation Facilities | FORMULA-PREP | Infant Feeding Preparation Facilities [FORMULA-PREP] | 2.2-2.8.8.17
Clinical Support | Interview Space | INTVW | Interview Space [INTVW] | 2.1-6.3.2 | Staff/patient conversation, screening
Clinical Support | Lactation Room | LACT | Lactation Room [LACT] | 2.2-2.8.8.16 | Non-staff, in NICU
Clinical Support | Laundry Processing | LDRY-PRCS | Laundry Processing [LDRY-PRCS] | 2.1-5.2.2.2 | For a facility with on-site laundry services | Laundry processing room
Clinical Support | Library | LIB | Library [LIB] | Not covered in FGI
Clinical Support | Linen Cart Storage Area | STRG-LINEN-CART | Linen Cart Storage Area [STRG-LINEN-CART] | 2.1-5.2.2.1 (4)
Clinical Support | Medical Equipment Shop | SHOP-MED-EQUIP | Medical Equipment Shop [SHOP-MED-EQUIP] | 2.1-5.6.5
Clinical Support | Medication Safety Zone | MEDS | Medication Safety Zone [MEDS] | 2.1-2.8.8 | Medication room or alcove | Medication room
Clinical Support | Milk Storage | STRG-MILK | Milk Storage [STRG-MILK] | 2.2-2.8.8.16 (2)(b)(i), 2.2-2.11.8.9
Clinical Support | Monitored Toilet Room | TLT-MONTRD | Monitored Toilet Room [TLT-MONTRD] | Outpatient 2.1-4.1.8.2 | Drug testing staff or non-staff | Patient toilet room
Clinical Support | Multipurpose Room | MTG-MULTIP | Multipurpose Room [MTG-MULTIP] | 2.1-4.2.8.3 | Possible in any department
Clinical Support | Nuclear Medicine Hot Lab | NUCMED-HOT | Nuclear Medicine Hot Lab [NUCMED-HOT] | 2.2-3.4.8.22 |  | Nuclear medicine hot lab
Clinical Support | Nurse Station | NSE-STN | Nurse Station [NSE-STN] | 2.1-2.8.2
Clinical Support | Nursery Workroom | NRSY-WRK | Nursery Workroom [NRSY-WRK] | 2.2-2.10.8.5 |  | Nursery workroom
Clinical Support | Patient Care Area Corridor | CORR | Patient Care Area Corridor [CORR] | 2.1-7.2.2.1, 2.1-7.2.2.2 (1), 2.1-7.2.2.10, 2.1-8.3.4.3 (2), 2.1-8.3.6.1, 2.1-8.5.1.2 (3)(a), 2.4-7.2.2, 2.5-8.3.4.2 (2) |  | Patient care area corridor
Clinical Support | Radiation Therapy Form Storage | STRG-FORM | Radiation Therapy Form Storage [STRG-FORM] | 2.2-3.5.3.4 (5), 2.2-3.5.4.6 (2)
Clinical Support | Radiation Therapy Mold Room | MOLD-RM | Radiation Therapy Mold Room [MOLD-RM] | 2.2-3.5.2.3 (1)
Clinical Support | Renal Dialysis Dialysate Preparation Room | DLYS-PREP | Renal Dialysis Dialysate Preparation Room [DLYS-PREP] | 2.2-3.10.8.17
Clinical Support | Renal Dialysis Dialyzer Reprocessing Room | DLYS-DIALYZER | Renal Dialysis Dialyzer Reprocessing Room [DLYS-DIALYZER] | 2.2-3.10.8.16 |  | Dialyzer reprocessing room
Clinical Support | Renal Dialysis Equipment Repair Room | DLYS-EQUIP-REPAIR | Renal Dialysis Equipment Repair Room [DLYS-EQUIP-REPAIR] | 2.2-3.10.8.19
Clinical Support | Soiled Holding | SOIL-HOLD | Soiled Holding [SOIL-HOLD] | 2.1-2.8.12.3 |  | Soiled holding room
Clinical Support | Soiled Linen Holding | SOIL-HOLD-LINEN | Soiled Linen Holding [SOIL-HOLD-LINEN] | 2.1-5.2.2.1 (1) | Sort and holding | Soiled holding room
Clinical Support | Soiled Tray Hold | SOIL-HOLD-TRAY | Soiled Tray Hold [SOIL-HOLD-TRAY] | 2.1-2.8.9.3
Clinical Support | Soiled Workroom | SOIL-WRK | Soiled Workroom [SOIL-WRK] | 2.1-2.8.12.2 |  | Soiled workroom
Clinical Support | Sterile Processing Clean Workroom | SP-CLN | Sterile Processing Clean Workroom [SP-CLN] | 2.1-5.1.2.2 (3) |  | Clean workroom
Clinical Support | Sterile Processing Decontamination Room | SP-DECON | Sterile Processing Decontamination Room [SP-DECON] | 2.1-5.1.2.2 (2) |  | Decontamination room
Clinical Support | Sterile Processing Room (one-room) | SP-PRCS | Sterile Processing Room (one-room) [SP-PRCS] | 2.1-5.1.2.3 | Only where countertop or similar-sized small sterilizers are used
Clinical Support | Sterile Storage | STRG-STRL | Sterile Storage [STRG-STRL] | 2.1-5.1.2.4 (1) |  | Sterile storage
Clinical Support | Sterile Supply Receiving | STRL-RECV | Sterile Supply Receiving [STRL-RECV] | 2.1-5.1.2.4 (2)
Clinical Support | Storage Clean Linen | STRG-LINEN | Storage Clean Linen [STRG-LINEN] | 2.1-2.8.13.1 | On patient floor, see also 2.1-5.2.2.1 (3) | Clean linen storage room
Clinical Support | Storage Emergency Equipment | STRG-EMER | Storage Emergency Equipment [STRG-EMER] | 2.1-2.8.13.4 | Code cart alcove
Clinical Support | Storage Patient Transport Equipment | STRG-PAT-TRNSP-EQUIP | Storage Patient Transport Equipment [STRG-PAT-TRNSP-EQUIP] | 2.1-2.8.13.3 | Wheelchair or gurney holding
Clinical Support | Surgery - Clean Equipment Supply Storage | STRG-CLN-EQUIP | Surgery - Clean Equipment Supply Storage [STRG-CLN-EQUIP] | 2.2-3.3.7.13 | May be the clean workroom of the satellite sterile processing facility (FGI Guidelines 2022)
Clinical Support | Surgery - Equipment Storage | STRG-EQUIP | Surgery - Equipment Storage [STRG-EQUIP] | 2.2-3.3.6.13, 2.2-3.3.8.13 (6)
Clinical Support | Surgery - Specimen Storage | STRG-SPECIMEN | Surgery - Specimen Storage [STRG-SPECIMEN] | 2.2-3.3.8.16
Clinical Support | System Component Room | COMPT | System Component Room [COMPT] | 2.2-3.3.4.6, 2.2-3.4.2.5 | Not exclusively imaging (although FGI references are imaging only)
Clinical Support | Ultrasound Probes Processing Facilities | PROBE-PRCS | Ultrasound Probes Processing Facilities [PROBE-PRCS] | 2.2-3.4.8.19 |  | Soiled workroom
D&T | Angiography Room | ANGIO | Angiography Room [ANGIO] | 2.2-3.4.2.1 (2) | Class 2 Imaging | Interventional imaging procedure
D&T | Audiology Testing | AUDIO | Audiology Testing [AUDIO] | 2.6-3.1.4.2
D&T | BMH Consult Room | CONS | BMH Consult Room [CONS] | 2.5-2.2.8.16
D&T | BMH Group Therapy Space | GROUP | BMH Group Therapy Space [GROUP] | 2.5-2.2.8.18
D&T | Bronchoscopy Procedure Room | BRONC | Bronchoscopy Procedure Room [BRONC] | 2.2-3.3.2.1 (1)(c) | Bronchoscopy, sputum collection, and pentamidine admin | Bronchoscopy, sputum collection, and pentamidine admin
D&T | Cardiac Stress Testing | STRESS-TEST | Cardiac Stress Testing [STRESS-TEST] | 2.2-3.4.7.1 (3)
D&T | Cesarean Delivery Room | C-SECT | Cesarean Delivery Room [C-SECT] | 2.2-2.9.11.1 |  | Cesarean delivery room
D&T | Computed Tomography (CT) Scan Room | CT | Computed Tomography (CT) Scan Room [CT] | 2.2-3.4.3.1 | Class 1 Imaging Class 2 Imaging | Imaging diagnostic and treatment Interventional imaging procedure
D&T | Consult Room | CONS | Consult Room [CONS] | 2.5-2.2.8.16
D&T | Consult/Demonstration Room | CONS-DEMO | Consult/Demonstration Room [CONS-DEMO] | 2.2-2.7.8.4
D&T | ECT Treatment Area | ECT | ECT Treatment Area [ECT] | 2.5-3.4.2 |  | ECT procedure room
D&T | ED Behavioral and Mental Health Treatment Room | ED-BMH-TRMT | ED Behavioral and Mental Health Treatment Room [ED-BMH-TRMT] | 2.2-3.1.4.3 (4) | Included in 2022 Guidelines | Treatment room
D&T | ED Flexible Secure Treatment Room | ED-SEC-TRMT | ED Flexible Secure Treatment Room [ED-SEC-TRMT] | 2.2-3.1.4.3 (2) | Included in 2022 Guidelines | Treatment room
D&T | ED Geriatric Treatment Room or Area | ED-GERI-TRMT | ED Geriatric Treatment Room or Area [ED-GERI-TRMT] | 2.2-3.1.3.6 (7) |  | Treatment room
D&T | ED Human Decontamination Area | ED-DECON | ED Human Decontamination Area [ED-DECON] | 2.2-3.1.3.6 (8) |  | ED human decontamination
D&T | ED Low-Acuity Patient Treatment Area | ED-LOW-ACU-TRMT | ED Low-Acuity Patient Treatment Area [ED-LOW-ACU-TRMT] | 2.2-3.1.3.6 (7) | Included in 2022 Guidelines
D&T | ED Reception and Triage Area | ED-TRIAGE | ED Reception and Triage Area [ED-TRIAGE] | 2.2-3.1.3.3 |  | Emergency service triage area
D&T | ED Secure Holding Room | ED-SEC-HOLD | ED Secure Holding Room [ED-SEC-HOLD] | 2.2-3.1.4.3
D&T | ED Trauma/Resuscitation Room | ED-TRAUMA | ED Trauma/Resuscitation Room [ED-TRAUMA] | 2.2-3.1.3.6 (4) |  | ED trauma/resuscitation room
D&T | ED Treatment Room | ED-TRMT | ED Treatment Room [ED-TRMT] | 2.1-3.2 |  | Treatment room
D&T | Endoscopy Procedure Room | ENDO | Endoscopy Procedure Room [ENDO] | 2.2-3.11.2 |  | Procedure room
D&T | Exam Room | EXAM | Exam Room [EXAM] | 2.1-3.2 |  | General examination room
D&T | Exam Room - AII | EXAM-AII | Exam Room - AII [EXAM-AII] | 2.2-3.1.4.2 |  | AII room
D&T | External Beam Radiation Therapy Room | EXT-BEAM-TRMT | External Beam Radiation Therapy Room [EXT-BEAM-TRMT] | 2.2-3.5.2.2
D&T | Fluoroscopy Room | FLUORO | Fluoroscopy Room [FLUORO] | 2.2-3.4.4.3 | Class 1 Imaging Class 2 Imaging Class 3 Imaging | Imaging diagnostic and treatment Interventional imaging procedure Operating room
D&T | Hybrid Operating Room | HYBRID-OR | Hybrid Operating Room [HYBRID-OR] | 2.2-3.3.4, 2.2-3.4.2 | Class 3 Imaging | Operating room
D&T | Hydrotherapy | HYDRO-TH | Hydrotherapy [HYDRO-TH] | 2.6-3.1.4.3 |  | Hydrotherapy
D&T | Hyperbaric Chamber | HYPERBARIC-CHMBR | Hyperbaric Chamber [HYPERBARIC-CHMBR] | 2.2-3.13.1.2
D&T | Hyperbaric Treatment Area | HYPERBARIC | Hyperbaric Treatment Area [HYPERBARIC] | 2.2-3.13
D&T | Imaging - Uptake/Cool down Room | WAIT-HOT | Imaging - Uptake/Cool down Room [WAIT-HOT] | 2.2-3.4.7.3 (6)
D&T | Infusion Area | INFUSION | Infusion Area [INFUSION] | 2.2-3.12.2
D&T | Labor/Delivery/Recovery Room | LDR | Labor/Delivery/Recovery Room [LDR] | 2.2-2.9.3 |  | Labor/delivery/recovery (LDR)
D&T | Labor/Delivery/Recovery/Postpartum Room | LDRP | Labor/Delivery/Recovery/Postpartum Room [LDRP] | 2.2-2.9.3 |  | Labor/delivery/recovery/postpartum (LDRP)
D&T | Magnetic Resonance Imaging (MRI) Scan Room | MRI | Magnetic Resonance Imaging (MRI) Scan Room [MRI] | 2.2-3.4.5.2 | Class 1 Imaging Class 2 Imaging Class 3 Imaging | Imaging diagnostic and treatment Interventional imaging procedure Operating room
D&T | Mammography Room | MAMMO | Mammography Room [MAMMO] | 2.2-3.4.4.4 | Class 1 Imaging Class 2 Imaging | Imaging diagnostic and treatment Interventional imaging procedure
D&T | MRI Patient Treatment / Resuscitation Area | MRI-EMER | MRI Patient Treatment / Resuscitation Area [MRI-EMER] | 2.2-3.4.5.6 |  | Imaging diagnostic and treatment
D&T | Multiple Modality Imaging Room | IMG-MULTI | Multiple Modality Imaging Room [IMG-MULTI] | 2.2-3.4.2.6
D&T | Nuclear imaging exercise area or room | NUCMED-EXER | Nuclear imaging exercise area or room [NUCMED-EXER] | 2.2-3.4.7.1 (3)
D&T | Nuclear Medicine Dose Administration Area | NUCMED-MEDS | Nuclear Medicine Dose Administration Area [NUCMED-MEDS] | 2.2-3.4.7.1 (5)
D&T | Occupational Therapy Area | OT | Occupational Therapy Area [OT] | 2.6-3.1.3
D&T | Operating Room | OR | Operating Room [OR] | 2.2-3.3.3 2.4-2.2.4.7 (3) |  | Operating Room
D&T | Phase I Post-Anesthetic Care Unit (PACU) | PACU | Phase I Post-Anesthetic Care Unit (PACU) [PACU] | 2.1-3.4.4 |  | Phase I PACU and Phase II recovery
D&T | Physical Therapy area | PT | Physical Therapy area [PT] | 2.6-3.1.2 |  | Physical therapy
D&T | Positron Emission Tomography (PET) Scan Room | PET | Positron Emission Tomography (PET) Scan Room [PET] | 2.2-3.4.7.3 (2) |  | Nuclear medicine procedure room
D&T | Post-Procedure Area – Phase II | POST | Post-Procedure Area – Phase II [POST] | 2.1-3.4.5
D&T | Pre-Post (Combined) Procedure Area | PREP-POST | Pre-Post (Combined) Procedure Area [PREP-POST] | 2.1-3.4.3 |  | Phase I PACU and Phase II recovery
D&T | Pre-Procedure Area | PREP | Pre-Procedure Area [PREP] | 2.1-3.4.3
D&T | Procedure Room | PROC | Procedure Room [PROC] | 2.2-3.3.2 | Outpatient setting when the room is used for multiple types of procedures | Procedure room
D&T | Proton Therapy Treatment Room | PROTON-TRMT | Proton Therapy Treatment Room [PROTON-TRMT] | 2.2-3.5.4.2 |  | Treatment room
D&T | Radiation Therapy | RAD-THERAPY | Radiation Therapy [RAD-THERAPY] | 2.2-3.5
D&T | Radiography Room | Based on actual procedure | Radiography Room [Based on actual procedure] | 2.2-3.4.4.2 | Class 1 Imaging | Imaging diagnostic and treatment
D&T | Radiosurgery Room (i.e., Gamma Knife) | Based on actual procedure | Radiosurgery Room (i.e., Gamma Knife) [Based on actual procedure] | 2.2-3.5.3.2 | Class 2 Imaging Class 3 Imaging | Interventional imaging procedure Operating room
D&T | Renal Dialysis - Hemodialysis Treatment Area | DLYS-TRMT | Renal Dialysis - Hemodialysis Treatment Area [DLYS-TRMT] | 2.2-3.10.2 |  | Dialysis treatment area
D&T | Renal Dialysis - Home Training Room | DLYS-EDUC | Renal Dialysis - Home Training Room [DLYS-EDUC] | 2.2-3.10.3
D&T | Scintigraphy Room | GAMMA-SCAN | Scintigraphy Room [GAMMA-SCAN] | 2.2-3.4.7.2 |  | Nuclear medicine procedure room
D&T | Sexual Assault Forensic Exam Room | SAFE | Sexual Assault Forensic Exam Room [SAFE] | 2.1-3.2.4
D&T | Single-photon emission computed tomography (SPECT) Room | SPECT | Single-photon emission computed tomography (SPECT) Room [SPECT] | 2.2-3.4.7.4 |  | Nuclear medicine procedure room
D&T | Speech Therapy | SPEECH | Speech Therapy [SPEECH] | 2.6-3.1.4.2
D&T | Telemedicine Provider Room | TELEMED-PROVIDER | Telemedicine Provider Room [TELEMED-PROVIDER] | Not covered in FGI
D&T | Telemedicine Room | TELEMED-EXAM | Telemedicine Room [TELEMED-EXAM] | 2.1-3.3.2
D&T | Ultrasound Room | USOUND | Ultrasound Room [USOUND] | 2.2-3.4.6.1 | Class 1 Imaging Class 2 Imaging | Imaging diagnostic and treatment Interventional imaging procedure
Family Support | BMH Visitor Room | VIS | BMH Visitor Room [VIS] | 2.5-2.2.10.1
Family Support | BMH Visitor Storage | STRG-VIS | BMH Visitor Storage [STRG-VIS] | 2.5-2.2.10.5
Family Support | Entry Vestibule | VESTB | Entry Vestibule [VESTB] | 2.5-2.2.1.2, 2.5-2.5-1.2 | Behavioral health and other secured areas
Family Support | Family and Visitor Communication | FAM-VIS-COMM | Family and Visitor Communication [FAM-VIS-COMM] | 2.1-2.10.1.6 2.2-2.3.10.3 (1)
Family Support | Family and Visitor Lounge | FAM-VIS-LNGE | Family and Visitor Lounge [FAM-VIS-LNGE] | 2.1-2.10.1
Family Support | Family and Visitor Waiting Area | FAM-VIS-WAIT | Family and Visitor Waiting Area [FAM-VIS-WAIT] | 2.2-3.3.10.4
Family Support | Family Respite | FAM-RESPITE | Family Respite [FAM-RESPITE] | 2.2-2.2.3, 2.2-2.11.3
Family Support | Family Shower | SHWR-FAM | Family Shower [SHWR-FAM] | A2.2-2.2.3.1-d
Family Support | Family Toilet | TLT-FAM | Family Toilet [TLT-FAM] | 2.2-2.11.3 |  | Toilet room
Family Support | Family Toilet/Shower | TLT-SHWR-FAM | Family Toilet/Shower [TLT-SHWR-FAM] | Not covered in FGI |  | Toilet room
Family Support | Meditation and Prayer Space | RESPITE | Meditation and Prayer Space [RESPITE] | 2.2-2.2.10.4 | Also: Respite space
Food Service | Dining Area | DINING | Dining Area [DINING] | 2.1-4.3.5 | Also: Cafeteria, snack bar, etc.
Food Service | Food and Supply Storage | STRG-FOOD | Food and Supply Storage [STRG-FOOD] | 2.1-4.3.8.13 |  | Food supply and storage
Food Service | Food Assembly and Distribution Facilities | FOOD-PRCS | Food Assembly and Distribution Facilities [FOOD-PRCS] | 2.1-4.3.3
Food Service | Food Support-EVS | EVS | Food Support-EVS [EVS] | 2.1-4.3.8.14
Food Service | Preparation Area | FOOD-PREP | Preparation Area [FOOD-PREP] | 2.1-4.3.2 |  | Food preparation areas
Food Service | Receiving Area | FOOD-RECV | Receiving Area [FOOD-RECV] | 2.1-4.3.8.1
Food Service | Refrigerated Storage | STRG-REF | Refrigerated Storage [STRG-REF] | 2.1-4.3.8.13 (2) |  | Food supply and storage
Food Service | Trash Storage | STRG-TRASH | Trash Storage [STRG-TRASH] | 2.1-4.3.8.16
Food Service | Ware Washing Facilities | WARE-WASH | Ware Washing Facilities [WARE-WASH] | 2.1-4.3.4 |  | Warewashing
Patient Care | Antepartum Room | ANTEPARTUM | Antepartum Room [ANTEPARTUM] | 2.2-2.9.2.1
Patient Care | BMH Patient Bedroom | PAT-RM | BMH Patient Bedroom [PAT-RM] | 2.5-2.2.2
Patient Care | Continuing Care Nursery | NRSY-CC | Continuing Care Nursery [NRSY-CC] | 2.2-2.10.3.2 |  | Continued care nursery
Patient Care | Intensive Care - Patient Room | ICU | Intensive Care - Patient Room [ICU] | 2.2-2.6.2.2 (1) |  | Intensive care patient care station
Patient Care | Intermediate Care Room | IMC | Intermediate Care Room [IMC] | 2.2-2.5.2 |  | Intermediate care patient room
Patient Care | Medical Psychiatric Patient Room | PAT-RM-BMH | Medical Psychiatric Patient Room [PAT-RM-BMH] | 2.2-2.2.4.6
Patient Care | Newborn Nursery | NRSY | Newborn Nursery [NRSY] | 2.2-2.10.3.1 |  | Newborn nursery
Patient Care | NICU AII | NICU | NICU AII [NICU] | 2.2-2.8.4.2 |  | AII room
Patient Care | NICU Multiple-Infant Room | NICU-MULTI | NICU Multiple-Infant Room [NICU-MULTI] | 2.2-2.8.2 |  | Neonatal intensive care
Patient Care | NICU Parent/Infant Room | NICU-PARENT | NICU Parent/Infant Room [NICU-PARENT] | 2.2-2.8.10.2 |  | Neonatal intensive care
Patient Care | NICU Single-Infant Room | NICU-SINGLE | NICU Single-Infant Room [NICU-SINGLE] | 2.2-2.8.2 |  | Neonatal intensive care
Patient Care | Patient Observation Station | OBS | Patient Observation Station [OBS] | 2.2-3.2.2, 2.2-2.17.2 (2022 Guidelines) | Second FGI reference is to behavioral health crisis unit
Patient Care | Patient Room | PAT-RM | Patient Room [PAT-RM] | 2.1-2.2 |  | Patient room
Patient Care | Patient Room – Airborne infection isolation (AII) | PAT-RM-AII | Patient Room – Airborne infection isolation (AII) [PAT-RM-AII] | 2.1-2.4.2 |  | AII room
Patient Care | Patient Room - Burn Trauma Intensive Care | PAT-RM-BURN | Patient Room - Burn Trauma Intensive Care [PAT-RM-BURN] | 2.2-2.16 (2022 Guidelines) |  | Wound intensive care (burn unit)
Patient Care | Patient Room - Combination AII/PE | PAT-RM-AII-PE | Patient Room - Combination AII/PE [PAT-RM-AII-PE] | 2.2-2.2.4.5 |  | Combination AII/PE anteroom
Patient Care | Patient Room - PE | PAT-RM-PE | Patient Room - PE [PAT-RM-PE] | 2.2-2.2.4.3 |  | Protective environment room
Patient Care | Postpartum Room | POSTPARTUM | Postpartum Room [POSTPARTUM] | 2.2-2.9.2.2 |  | Patient room
Patient Care | Seclusion Room | SECLUSION | Seclusion Room [SECLUSION] | 2.1-2.4.3 |  | Seclusion room
Patient Support | BMH Child Activity Area | ACTIVITY-CHILD | BMH Child Activity Area [ACTIVITY-CHILD] | 2.5-2.3.3
Patient Support | BMH Kitchenette | PAT-KIT | BMH Kitchenette [PAT-KIT] | 2.5-2.2.8.9 (2)
Patient Support | BMH Patient Bathing Facilities | PAT-TUB | BMH Patient Bathing Facilities [PAT-TUB] | 2.5-2.2.2.7
Patient Support | BMH Patient Laundry Facilities | PAT-LDRY | BMH Patient Laundry Facilities [PAT-LDRY] | 2.5-2.2.10.3
Patient Support | BMH Patient Storage | STRG-PAT | BMH Patient Storage [STRG-PAT] | 2.5-2.2.2.8
Patient Support | BMH Patient Toilet Room | TLT-PAT | BMH Patient Toilet Room [TLT-PAT] | 2.5-2.2.2.6 |  | Patient toilet room
Patient Support | BMH Quiet Room | QUIET-RM | BMH Quiet Room [QUIET-RM] | 2.5-2.2.4.4
Patient Support | BMH Social Space | SOCIAL | BMH Social Space [SOCIAL] | 2.5-2.2.10.2
Patient Support | Nourishment Area or Room | NOUR | Nourishment Area or Room [NOUR] | 2.1-2.8.9 |  | Nourishment area or room
Patient Support | Outdoor - Activity Area | ACTIVITY-OUTDR | Outdoor - Activity Area [ACTIVITY-OUTDR] | 2.5-2.2.3
Patient Support | Patient Bathing Facilities (Central) | PAT-TUB | Patient Bathing Facilities (Central) [PAT-TUB] | 2.2-2.2.2.7 (2)
Patient Support | Patient Belonging Storage | STRG-PAT | Patient Belonging Storage [STRG-PAT] | 2.6-2.2.2.8, 2.1-2.2.8
Patient Support | Patient Changing Room or Area | PAT-DRESS | Patient Changing Room or Area [PAT-DRESS] | 2.2-3.3.10.3, 2.2-3.4.10.3
Patient Support | Patient Gowned Waiting Area | PAT-WAIT-GOWNED | Patient Gowned Waiting Area [PAT-WAIT-GOWNED] | 2.2-3.3.10.3, 2.2-3.4.10.3
Patient Support | Patient Locker | PAT-LCKR | Patient Locker [PAT-LCKR] | 2.2-3.3.10.3 (1)(a), 2.2-3.4.10.3 (3)
Patient Support | Patient Play Area | PLAY | Patient Play Area [PLAY] | 2.2-2.4.10.1, 2.7-2.2.8.16
Patient Support | Patient Shower | SHWR-PAT | Patient Shower [SHWR-PAT] | 2.2-2.2.2.7 (1)(a) |  | Patient toilet room
Patient Support | Patient Toilet Room | TLT-PAT | Patient Toilet Room [TLT-PAT] | 2.1-2.2.6 |  | Patient toilet room
Patient Support | Patient Toilet/Shower | TLT-SHWR-PAT | Patient Toilet/Shower [TLT-SHWR-PAT] | 2.2-2.2.2.7 (1)(a) |  | Patient toilet room
Patient Support | Patient Waiting Area | PAT-WAIT | Patient Waiting Area [PAT-WAIT] | 2.2-3.4.10.1
Patient Support | Rehabilitation - Patient Living Area | PAT-LIVING | Rehabilitation - Patient Living Area [PAT-LIVING] | 2.6-2.3 | Resident gathering/activity/ dining
Patient Support | Skilled Nursing - Dining and Recreation Spaces | PAT-DINING | Skilled Nursing - Dining and Recreation Spaces [PAT-DINING] | 2.2-2.13.10.1 | Also used in behavioral health facilities
Patient Support | Skilled Nursing - Patient Grooming Room | PAT-GROOM | Skilled Nursing - Patient Grooming Room [PAT-GROOM] | 2.2-2.13.10.3
Public and Admin Areas | Above Ground Building Connector | CONNECTOR | Above Ground Building Connector [CONNECTOR] | Not covered in FGI
Public and Admin Areas | Atrium | ATRIUM | Atrium [ATRIUM] | Not covered in FGI
Public and Admin Areas | Auditorium | MTG-AUDITORIUM | Auditorium [MTG-AUDITORIUM] | Not covered in FGI
Public and Admin Areas | Communicating Stairway | STAIR | Communicating Stairway [STAIR] | Not covered in FGI
Public and Admin Areas | Conference Room | MTG-CONF | Conference Room [MTG-CONF] | Not covered in FGI
Public and Admin Areas | Corridor | CORR | Corridor [CORR] | 2.1-7.2.2.1, 2.1-7.2.2.2 (1), 2.1-8.3.6.1, 2.4-7.2.2 | This is different from Patient Care Area Corridor
Public and Admin Areas | Egress Stairway | STAIR | Egress Stairway [STAIR] | Not covered in FGI
Public and Admin Areas | Elevator Lobby | LOBBY-ELEV | Elevator Lobby [LOBBY-ELEV] | 2.1-6.2.2
Public and Admin Areas | Elevators | ELEV | Elevators [ELEV] | 2.1-8.7.2
Public and Admin Areas | Lecture Hall | MTG-LECTURE | Lecture Hall [MTG-LECTURE] | Not covered in FGI
Public and Admin Areas | Lobby | LOBBY | Lobby [LOBBY] | 2.1-6.2.2
Public and Admin Areas | Outdoor - Emergency Access | EMER-ACCESS-OUTDR | Outdoor - Emergency Access [EMER-ACCESS-OUTDR] | 1.3-3.5
Public and Admin Areas | Outdoor - Landscape | LANDSCAPE | Outdoor - Landscape [LANDSCAPE] | 1.3-3.6.2
Public and Admin Areas | Outdoor - Water Feature | LANDSCAPE-WATER | Outdoor - Water Feature [LANDSCAPE-WATER] | 1.3-3.6.1
Public and Admin Areas | Parking garage | GARAGE | Parking garage [GARAGE] | 1.3-3.5
Public and Admin Areas | Parking Surface Lot | LOT | Parking Surface Lot [LOT] | 1.3-3.4
Public and Admin Areas | Public Toilet Room | TLT-PUB | Public Toilet Room [TLT-PUB] | 2.1-6.2.3
Public and Admin Areas | Reception | RECP | Reception [RECP] | 2.1-6.2.3
Public and Admin Areas | Retail | RETAIL | Retail [RETAIL] | Not covered in FGI
Public and Admin Areas | Roads and Walkways | ROAD | Roads and Walkways [ROAD] | 1.3-3.3
Public and Admin Areas | Vehicular Drop-Off | DROP-OFF | Vehicular Drop-Off [DROP-OFF] | 2.1-6.2.1
Public and Admin Areas | Vending Machine Area | VENDING | Vending Machine Area [VENDING] | 2.1-4.3.6
Public and Admin Areas | Waiting Room or Area | WAIT | Waiting Room or Area [WAIT] | 2.1-6.2.3
Staff Support | Changing Area | STAFF-DRESS | Changing Area [STAFF-DRESS] | 2.2-2.9.11.9 (3), 2.2-3.3.9.4
Staff Support | Changing Area - Toilet/Shower | TLT-SHWR-STAFF-DRESS | Changing Area - Toilet/Shower [TLT-SHWR-STAFF-DRESS] | 2.2-2.9.11.9 (3)(b), 2.2-3.3.9.4 (2) |  | Toilet room
Staff Support | Lactation Room | STAFF-LACT | Lactation Room [STAFF-LACT] | 2.1-6.4.3 (2022 Guidelines)
Staff Support | Locker | LCKR | Locker [LCKR] | 2.1-2.9.3
Staff Support | Lounge | LNGE | Lounge [LNGE] | 2.1-2.9.1
Staff Support | Office | OFF OFF-PVT OFF-SHRD | Office [OFF OFF-PVT OFF-SHRD] | 2.1-2.8.4 | Category can be used for staff work spaces in other areas
Staff Support | Resident Workroom | WRK-RESIDENT | Resident Workroom [WRK-RESIDENT] | Not covered in FGI | Room required for graduate medical education
Staff Support | Respite | RESPITE | Respite [RESPITE] | Not covered in FGI | For staff (for patient and family, refer to 2.2-2.2.10.4)
Staff Support | Staff On-Call Sleep Rooms | ON-CALL | Staff On-Call Sleep Rooms [ON-CALL] | 2.2-2.6.9.4 | Allows use where facilities have sleep rooms for staff other than 24hr. shift staff
Staff Support | Staff Toilet Room | TLT-STAFF | Staff Toilet Room [TLT-STAFF] | 2.1-2.9.2 |  | Toilet room
Notes
1. This table includes some spaces that are not covered in the FGI Guidelines. The added spaces cover commonly expected spaces in hospitals and are included here
so this classification schema can be used “as is” to support functional programming and operational space management (FGI 1.2-2.1.3.1)
2. Abbreviations are intended for use on drawings. They are not distinct since the drawings will provide necessary context.
For programming, the use of the full space name is recommended.
Each drawing set should contain an abbreviation legend.
3. To measure net square footage (NSF) for spaces, use of the process of NSF provided in the 2017 ASHE Monograph “Area Calculation Method for Health Care” is
recommended. (https://www.ashe.org/areacalculation)
Definitions of Groupings
Grouping | Definitions
Building Support | Spaces critical for maintaining a structurally sound, safe, and operational built environment
Clinical Services | Spaces where physicians’ orders for medications and clinical specimen testing are completed and documented in the medical record
Clinical Support | Spaces for functions that provide services and goods in support of patient care and clinical services
Diagnostic and Treatment Areas | Spaces where patient encounters occur for diagnosis and/or treatment under the direction of medical staff
Family Support | Spaces designated for the needs of patients’ family, partners, and extended visitors
Food and Nutrition Services | Spaces required for activities that facilitate consumption of food for all people in the facility
Patient Care | Spaces where patients are based in a patient care unit after admitted for medical care and related patient care spaces serving the unit
Patient Support | Spaces that provide for the personal needs of patients (e.g., hygiene, nourishment, storage of personal property)
Public and Administrative Areas | Spaces provided for the business and public interface of a facility
Staff Support | Spaces that provide for the personal needs of facility personnel (e.g., hygiene, nourishment, storage of personal property)
Abbreviation Elements
The table below provides a toolkit of suggested abbreviations.
The toolkit was used in the development of the abbreviations for the FGI Space Categorization.
Abbreviation | Represented by Abbreviation | Comment
ACC | Accessibility Code Compliant | Used when there are accessibility codes to be followed in addition to those in the ADA.
Acu | Acuity
Admit | Admissions function
AII | Airborne Infection Isolation
Amenity | Function is for comfort of user, not clinical
Anes | Anesthesia or related to
Angio | Angiography
Ante | Ante room an entry into a controlled environment room
Audio | Audiology or related to
Bari | Bariatric. Patient of Size per FGI 2018
Bay | One hard wall and 3 soft (curtains or moveable partitions)
BioHaz | Biohazard. Waste containing/ has come into contact with bacteria or other pathogens, blood, or body fluids.
BMH | Behavioral and/or Mental Health
Bronc | Bronchoscopy or related to
Bus | Business function, clerical
C-Sect | Caesarean Section
Cart | Portable supply carts, clinical or materials
Circ | Circulation
Class | Classroom, Education
Cln | Clean, particularly related to supplies
Clin | Clinical
Coll | Collection
Comm | Communication
Comp | Compounding
Compt | Component. Electrical components required for larger imaging equipment
Conf | Conference, meeting etc.
Cons | Consult
Cplt | Couplet. Maternal-Newborn care
Corr | Corridor
CT | CT Scan or related to
C-Sect | C-Section
Ctr | Central
Ctrl | Control of entry, or observation during procedures.
Cube | Cubicle. Enclosed on 3 sides with full- or partial-height soft walls
Dir | Director
D&T | Diagnostic and/or Treatment
Dbl | Double
Decon | Decontamination
Dine | Dining Area
Disp | Dispensing or Dispensary
Docum | Documentation
Dlys | Dialysis
Dress | Dressing or Changing
Dumbw | Dumbwaiter
ECT | Electro convulsive therapy
Educ | Education, training
Elec | Electric
| Elec-Emer | Emergency Power
EEG | Electroencephalogram
EKG | Electrocardiogram
Elec | Electrical or related to
Elev | Elevator
EMG | Electromyogram
Endo | Endoscopy or related to
Esc | Escalator
Emer | Emergency
Equip | Equipment
EVS | Environmental Services
Exam | Examination Room
Exec | Executive
Ext | External
Extr | Exterior
F | Female
Fam | Family
Fluoro | Fluoroscopy or related to
FM | Facilities Management
Food | related to Food and Nutrition Services
Form | Formula or Form
FP | Fire protection or related to
Frz | Freezer or Frozen
Gas | Gases
Gen | Generator or General
Geri | Geriatric
Groom | Grooming as in hair salon, barber etc.
Haz | Hazard
HIM | Health Information Management, Medical Records
Hndwash | Handwashing sink location
Hport | Heliport
Hold | Temporary location, typically storage
Hot | Radioactive
ICU | Intensive Care Unit
IMC | Intermediate Care Room
Img | Imaging
Infra | Infrastructure
Intvl | Interventional
Intvw | Interview
IV | Intravenous
Iso | Isolation
Kit | Kitchen, Kitchenette
Lact | Lactation
LDR | Labor and Delivery Rm
LDRP | Labor and Delivery Postpartum Rm
Lib | Library
Linac | Linear Accelerator
Lckr | Locker
Ldry | Laundry
Lnge | Lounge
M | Male
Mammo | Mammography
Mech | Mechanical or mechanical related
Med | Medical
Meds | Medication
Mgmt | management
MM | Materials Management
Montrd | Monitored
Mtg | Meeting, conference, multipurpose
Mgr | Manager
Neg | Negative Air Pressure
Nour | Nourishment
Nse | Nurse
Nse Stn | Nurse Station
Nsry | Nursery | Open room with multiple stations for well-born infant care
NucMed | Nuclear Medicine or related to
Obs | Observation
Off | Office
Off-Pvt | Private Office
Off-Shrd | Shared Office
Off-Mgr | Manager's Office
OT | Occupational Therapy
Outdr | Outdoor
PACU | PACU
Pat | Patient
Pat Rm | Refers to Single Bed Inpatient & Outpatient
Pat Rm-Dbl | Refers to 2 Bed Inpatient & Outpatient
Pat Rm-Iso | Pat Room Isolation, Not Negative Aire
Pat Rm-Multi | Refers to 3 or more beds Inpatient & Outpatient
Pat Rm-Neg | Patient Room Negative Air
Pedi | Pediatric, Children or Child
Pharm | Pharmacy
Phleb | Phlebotomy
Plbg | Plumbing or plumbing related
Pos | Positive Air Pressure
Prcs | Process
Pre | Pre-procedure
Prep | Preparation
Proc | Procedure. Care that requires high-level disinfection or sterile instruments & some environmental controls but not the environmental controls of an OR.
PE | Protective Environment
Post | After
PPEDD | PPE Donning and Doffing area
Prov | Provider
PFT | Pulmonary Function Test
PT | Physical Therapy
Pub | Public
Pvt | Private
Rad | Radiation or Radical
Rcvry | Recovery
Recp | Reception
Recv | Receiving
Ref | Refrigerator, Refrigerated
Reg | Registration, Checkin/out
Respt | Respite, bereavement
Rm | Room. A space with 4 walls and a means of entry/exit.
SAFE | Sexual Abuse Forensic Exam
Sec | Secure or Security
Sgl | Single
Shwr | Shower
Shop | Area for repair, refurbishing, refinishing specific to a trade
Sleep | A room for sleeping other than patients
Sleep | Prov-Sleep | Provider Sleeping Room
Sleep | Fmly-Sleep | Family Sleeping Room
Soil | Soiled
SP | Sterile processing
Staff | Staff
Stn | Station
Strl | Sterile or Substerile, spaces that are under strict cleanliness standards
Strg | Storage
Strg-Cln | Clean Storage
Strg-Equip | Equipment Storage
Strg-Linen | Linen Storage
Strg-Soil | Soiled Storage
Strg-Supply | Supply Storage
Surg | Surgical
Supt | Support
Sply | Supply
Shrd | Shared
Task | Process of turnaround for an item
Test | Testing or Test
Tlt | Toilet
Tlt-Fam | Single seat room for family, but not patient use. Uncommon unless it is part of a family lounge
Tlt-Pat | Single seat room for patient use
Tlt-Public | Single or multiple stall for public use, typically at waiting Rooms
Tlt-Staff | Single or multiple stall for staff use
Tlt-U | Non-gender specific, typically private single toilet room
Trmt | Treatment
Tub | Bathing room
Usound | Ultrasound
Util | Utility, as in electric utility
Vest | Vestibule
Vis | Visitor
Wait | Waiting, subwaiting, gowned waiting
Wash | Washing or related to
WCh | Wheelchair
Wrk | Work
Wrk-Staff | Open area for staff to work typically unassigned
WrkStn | Work Station
Wrk-Team | Team Work
Xfer | Transfer

## 4) Building Systems
Data Standardization in Health Care Facility Management |  | Source: CSI Uniformat 2010 | https://www.csiresources.org/standards/uniformat
Categorization of Building Systems |  |  | The trademark UNIFORMAT© and the copyrighted UNIFORMAT work are used under license from CSI (http://www.csiresources.org).
Version 0.9
UniFormat Ref. | Functional Element or Building System | Reference One-Line Drawing (See Tab 6) | Notes
A10 | A. Substructure - Foundation - (System) Foundation | Not on schematic
B10 | B. Shell - Superstructure - (System) Building | Not on schematic
B10 | B. Shell - Superstructure - (System) Parking Structure | Not on schematic
B20 | B. Shell - Vertical Enclosures - (System) Façades and Windows | Not on schematic
B30 | B. Shell - Roof - (System) Roof | Not on schematic
C1010 | C. Interiors - Barrier Walls - (System) Barrier Walls | C10-1 Barrier Walls
C1030 | C. Interiors - Doors - (System) Doors | Not on schematic
C10a | C. Interiors - Rooms - (System) Room without Env. Controls | Not on schematic
C10b | C. Interiors - Rooms with Env. Controls - (System) Rooms with Env. Controls | Not on schematic
D1010 | D. Services - Conveying - Vertical Transportation - (System) Elevators | Not on schematic
D1050.40 | D. Services - Conveying - Material Handling - (System) Conveyor | Not on schematic
D1050.60 | D. Services - Conveying - Material Handling - (System) Linen Chute | D10-2 Chutes
D1050.60 | D. Services - Conveying - Material Handling - (System) Trash Chute | D10-2 Chutes
D1050.70 | D. Services - Conveying - Material Handling - (System) Pneumatic Tube | D10-1 Pneumatic Tube System
D1080.50 | D. Services - Conveying - Operable Access Systems - (System) Window Cleaning | Not on schematic
D2010 | D. Services - Plumbing - Domestic Water - (System) Domestic Hot Water | D20-1 Domestic Water
D2010 | D. Services - Plumbing - Domestic Water - (System) Domestic Water | D20-1 Domestic Water
D2010.20 | D. Services - Plumbing - Domestic Water - (System) Water Treatment and Filtration | Not on schematic
D2020 | D. Services - Plumbing - Sanitary Drainage - (System) Sanitary Drainage | Not on schematic
D2050 | D. Services - Plumbing - Control Air - (System) Control Air | Not on schematic
D2060.10a | D. Services - Plumbing - Lab Air - (System) Laboratory Air | D20-2 Lab Air
D2060.10b | D. Services - Plumbing - Medical Air - (System) Medical Air | D20-3 Medical Air
D2060.20a | D. Services - Plumbing - Lab Vacuum - (System) Laboratory Vacuum | D20-4 Medical-Lab Vacuum
D2060.20b | D. Services - Plumbing - Medical Vacuum - (System) Medical Vacuum | D20-4 Medical-Lab Vacuum
D2060.20c | D. Services - Plumbing - WAGD Vacuum - (System) Waste Anesthesia Gas Disposal | D20-5 WAGD Vacuum
D2060.30a | D. Services - Plumbing - Oxygen Gas - (System) Oxygen Gas | D20-6 Medical Gas Oxygen
D2060.30b | D. Services - Plumbing - Nitrogen Gas - (System) Nitrogen Gas | D20-7 Medical Gas Nitrogen
D2060.30c | D. Services - Plumbing - Nitrous Oxide Gas - (System) Nitrous Oxide Gas | D20-8 Medical Gas Nitrous Oxide
D2060.30d | D. Services - Plumbing - Carbon Dioxide Gas - (System) Carbon Dioxide Gas | D20-9 Medical Gas Carbon Dioxide
D2060.40 | D. Services - Plumbing - Chemical-Waste Systems - (System) Chemical Waste | Not on schematic
D2060.50 | D. Services - Plumbing - Processed Water - (System) Water Purification - Deionized Water (DI) | Not on schematic
D2060.50 | D. Services - Plumbing - Processed Water - (System) Water Purification - Reverse Osmosis (RO) | Not on schematic
D2060.90 | D. Services - Plumbing - Heat Trace System - (System) Heat Trace | Not on schematic
D3020.10 | D. Services - HVAC - Central Heating - (System) Central Heating | D30-1 Steam Heating and Distribution D30-2 Hydronic Central Heating
D3020.70 | D. Services - HVAC - Decentralized Heating - (System) Decentralized Heating | D30-3a Hydronic Central Cooling D30-3b Air Cooled Chiller
D3030.10 | D. Services - HVAC - Central Cooling - (System) Central Cooling | Not on schematic
D3030.70 | D. Services - HVAC - Decentralized Cooling - (System) Decentralized Cooling | Not on schematic
D3030.70 | D. Services - HVAC - Decentralized Cooling - (System) Split Type | Not on schematic
D3050.10 | D. Services - HVAC - Hydronic Distribution - (System) Hydronic Distribution | D30-2 Hydronic Central Heating D30-3 Hydronic Central Cooling | Hydronic distribution is typically tracked as part of Central Heating or Cooling System
D3050.30 | D. Services - HVAC - Steam Distribution - (System) Steam Distribution | D30-1 Steam Heating and Distribution | Steam distribution is typically tracked as part of Central Heating System
D3050.50 | D. Services - HVAC - Air Handling - (System) Air Distribution | D30-5 HVAC Air Handling
D3060.30 | D. Services - HVAC - Ventilation - Exhaust Air - (System) Exhaust Air | Not on schematic
D3070.10 | D. Services - HVAC - Snow Melting - (System) Snow Melting | Not on schematic
D4010.10 | D. Services - Fire Protection, Water-Based - (System) Sprinkler, Dry Pipe | D40-1a Fire Risers D40-1b Fire Pumps D40-1c House Tanks
D4010.10 | D. Services - Fire Protection, Water-Based - (System) Sprinkler, Pre-action | D40-1a Fire Risers D40-1b Fire Pumps D40-1c House Tanks
D4010.10 | D. Services - Fire Protection, Water-Based - (System) Sprinkler, Wet Pipe | D40-1a Fire Risers D40-1b Fire Pumps D40-1c House Tanks
D4010.10 | D. Services - Fire Protection, Water-Based - (System) Standpipe | D40-1a Fire Risers D40-1b Fire Pumps D40-1c House Tanks
D4010.10 | D. Services - Fire Protection, Water-Based - (System) Water Mist Extinguishing | D40-1a Fire Risers D40-1b Fire Pumps D40-1c House Tanks
D4010.50 | D. Services - Fire Protection, Non-Water-Based - (System) Dry Chemical Extinguishing | Not on schematic
D4010.50 | D. Services - Fire Protection, Non-Water-Based - (System) Gaseous Extinguishing | Not on schematic
D4010.50 | D. Services - Fire Protection, Non-Water-Based - (System) Kitchen Extinguishing | Not on schematic
D4010.50 | D. Services - Fire Protection, Non-Water-Based - (System) Wet Chemical Extinguishing | Not on schematic
D5010 | D. Services - Electrical Power Generation - (System) Power Generation | D50-1 Electrical Power Generation | Is typically tracked with the Emergency branch of the Electrical Service and Distribution "system"
D5020.10 | D. Services - Electrical Service and Distribution - (System) Electrical Service and Distribution | D50-2a Electrical Power Distribution D50-2b Electrical Power Distribution D50-2c Electrical Power Distribution
D5040.50 | D. Services - Electrical Lighting Fixtures - (System) Emergency Lighting | D50-3 Emergency Lighting
D6020.20a | D. Services - Communications - Radio - (System) Radio | Not on schematic
D6020.20b | D. Services - Communications - Telephone - (System) Telephone | Not on schematic
D6030.10 | D. Services - Communications - Audio - (System) Audio | Not on schematic
D6060.30a | D. Services - Communications - Nurse Call - (System) Nurse Call | Not on schematic
D6060.30b | D. Services - Communications - RTLS - (System) Remote Telemetry Location System | Not on schematic
D6060.50 | D. Services - Communications - Clock System - (System) Clock | Not on schematic
D7050.10 | D. Services - Detection and Alarm - Fire Protection - (System) Fire Alarm | D70-1 Fire Detection and Alarm
D8010 | D. Services - Integrated Automation - (System) Integrated Automation Facilities Controls | Not on schematic
E1010.10 | E. Equipment - Vehicles - (System) Vehicles | Not on schematic
E1010.30 | E. Equipment - Vehicles - (System) Parking Control | Not on schematic
E1010.50 | E. Equipment - Loading Dock - (System) Loading Dock | Not on schematic
E1030.35 | E. Equipment - Laundry - (System) Laundry | Not on schematic
E1030.40 | E. Equipment - Maintenance - (System) Maintenance | Not on schematic
E1030.80 | E. Equipment - Foodservice - (System) Food Service | Not on schematic
E1040.10 | E. Equipment - Lab - (System) Lab | Not on schematic
E1040.20 | E. Equipment - Healthcare - (System) Healthcare | Not on schematic
E1090.10 | E. Equipment - Environmental Services - (System) Environmental Services | Not on schematic
E1090.60 | E. Equipment - Decontamination/Sterilization - (System) Decontamination / Sterilization | Not on schematic
F1050 | F. Special Features - Special Facility Components - (System) Special Facility Component | Not on schematic
F1050.10 | F. Special Features - Special Facility Components - (System) Pool | Not on schematic
G2080.10 | G. Site - Improvements - (System) Grounds | Not on schematic
G2080.10 | G. Site - Improvements - (System) Landscape Irrigation | Not on schematic
G3030 | G. Site - Storm Drainage - (System) Site Storm Drain | Not on schematic
G3050 | G. Site - Fuel Distribution - (System) Fuel Polishing System | Not on schematic
G3060.10 | G. Site - Natural/Propane Gas - (System) Natural/Propane Fuel | G-10 Site Fuel Distribution
G3060.20 | G. Site - Fuel Oil - (System) Fuel Oil | G-10 Site Fuel Distribution
G3060.30 | G. Site - Gasoline - (System) Gasoline | G-10 Site Fuel Distribution
G3060.40 | G. Site - Diesel - (System) Diesel | G-10 Site Fuel Distribution
G4010 | G. Site - Groundings - (System) Groundings / Lighting Protection | Not on schematic
G4050 | G. Site - Lighting - (System) Site Lighting | Not on schematic

## 4.1) Building Sys Dependencies
Building Systems and Their Dependencies Version 0.9 Follow the Row to see upstream relationships. Follow the Column to see downstream relationships. Building Systems | A - Foundation | B10 - Building | B10 - Parking Garage | B10 - Egress | B20 - Facades | B30 - Roof | C10 - Barrier Walls | D1010 - Vertical Transportation | D1050 - Pneumatic Tube System | D1050 - Chutes | D2010 - Domestic Water System | D2010 - Domestic Water System - Hot Water System | D2020 - Plumbing - Sanitary Drainage System | D2060.30 - Plumbing - Lab Air System | D2060.30 - Plumbing - Med Air System | D2060.30 - Plumbing - Lab Vacuum System | D2060.30 - Plumbing - Med Vacuum System | D2060.30 - Plumbing - WAGD Vacuum System | D2060.30 - Plumbing - Oxygen Gas System | D2060.30 - Plumbing - Nitrogen Gas System | D2060.30 - Plumbing - Nitrous Oxide Gas System | D2060.30 - Plumbing - Carbon Dioxide Gas System | D3020 - HVAC - Central Heating System | D3030 - HVAC - Central Cooling System | D3020 - HVAC - Decentralized Heating Systems | D3030 - HVAC - Decentralized Cooling Systems | D3050.10 - HVAC Hydronic Distribution System | D3050.30 - HVAC Steam Distribution System | D3050.50 - HVAC Air Distribution System | D4010.10 - Fire Protection, Water-Based | D4010.50 - Fire Protection, Non-Water Based | D5010.00 - Electrical Service / Facility Power Generation | D5020.10 - Electrical Service | D5020.30 - Electrical Power Distribution | D5040.50 - Emergency Lighting | D6060.30 - Audio System | D6060.30 - Nurse Call System | D6060.50 - Clock System System | D7050.10 - Fire Detection and Alarm System | D8010 - Integrated Automation Facility Controls | G20 - Site Improvements | G30 - Site Utilities | G3050 - Site Utilities - Fuel Distribution | G4050 - Site Lighting
A - Foundation
B10 - Building
B10 - Parking Garage
B10 - Egress
B20 - Facades
B30 - Roof
C10 - Barrier Walls
D1010 - Vertical Transportation
D1050 - Pneumatic Tube System
D1050 - Chutes
D2010 - Domestic Water System
D2010 - Domestic Water System - Hot Water System
D2020 - Plumbing - Sanitary Drainage System | [44 empty] | = Functionally Required Dependency Upstream
D2060.30 - Plumbing - Lab Air System | [44 empty] | = Functionally Required Dependency Upstream, depending on type of system
D2060.30 - Plumbing - Med Air System
D2060.30 - Plumbing - Lab Vacuum System | [44 empty] | = System can run semi-autonomously for a while
D2060.30 - Plumbing - Med Vacuum System | [44 empty] | = System can run semi-autonomously for a while, depending on type of system
D2060.30 - Plumbing - WAGD Vacuum System
D2060.30 - Plumbing - Oxygen Gas System
D2060.30 - Plumbing - Nitrogen Gas System
D2060.30 - Plumbing - Nitrous Oxide Gas System
D2060.30 - Plumbing - Carbon Dioxide Gas System
D3020 - HVAC - Central Heating System
D3030 - HVAC - Central Cooling System
D3020 - HVAC - Decentralized Heating Systems
D3030 - HVAC - Decentralized Cooling Systems
D3050.10 - HVAC Hydronic Distribution System
D3050.30 - HVAC Steam Distribution System
D3050.50 - HVAC Air Distribution System
D4010.10 - Fire Protection, Water-Based
D4010.50 - Fire Protection, Non-Water Based
D5010.00 - Electrical Service / Facility Power Generation
D5020.10 - Electrical Service
D5020.30 - Electrical Power Distribution
D5040.50 - Emergency Lighting
D6060.30 - Audio System
D6060.30 - Nurse Call System
D6060.50 - Clock System
D7050.10 - Fire Detection and Alarm System
D8010 - Integrated Automation Facility Controls
G20 - Site Improvements
G30 - Site Utilities
G3050 - Site Utilities - Fuel Distribution
G4050 - Site Lighting
https://www.csiresources.org/standards/uniformat
The trademark UNIFORMAT© and the copyrighted UNIFORMAT work are used under license from CSI (http://www.csiresources.org).
[37 empty] | Source: CSI Uniformat 2010 | [5 empty] | https://www.csiresources.org/standards/uniformat
The trademark UNIFORMAT© and the copyrighted UNIFORMAT work are used under license from CSI (http://www.csiresources.org).

## 5) Assets
Data Standardization in Health Care Facility Management | [11 empty] | Source: CSI Uniformat 2010 | https://www.csiresources.org/standards/uniformat
Categorization of Assets | [12 empty] | The trademark UNIFORMAT© and the copyrighted UNIFORMAT work are used under license from CSI (http://www.csiresources.org).
Version 0.9
Note: References to the Omniclass tables are incomplete
Type | CSI UniFormat 2010 | Reference to Schematics on Tab 6 | ASHE Asset Categories (with Simplified UniFormat Codes) | Level 1 - System / Subsystem | Level 2 - Maintainable Asset | Level 3 - Asset Type | ASHE Asset Categories (Plain Language) | Level 1 (System/Subsystem) | Level 2 (Maintainable Asset) | Level 3 (Asset Type) | Naming Convention | What is the asset? | How is it identified? | Asset Definition | Regulatory References The ASHE working group will add references to applicable national codes for each category. | OmniClass Table 21 Numbers | OmniClass Table 21 Titles | OmniClass Table 22 Numbers | OmniClass Table 22 Titles | OmniClass Table 23 Numbers | OmniClass Table 23 Titles | OmniClass Table 13 numbers | OmniClass Table 13 Titles
Grouping | A10 |  | A10 - Foundation | A10 - Foundation |  |  | A. Foundation | A. Foundation | [5 empty] | General Category |  | 21-02 10 | Superstructure
System | A10 | Not on One-Line | A10 - Foundation - (System) Foundation | A10 - Foundation | (System) Foundation |  | A. Foundation - (System) Foundation | A. Foundation | (System) Foundation |  | SYS Foundation | Each building | No barcode - Track by location | Generic representation of building foundation. |  | 21-01 10 | Foundations | 22-31 60 00
Supplemental Elements | A10.99 | n/a | A10 - Foundation - [Supplemental Elements] Foundation | A10 - Foundation | [Supplemental Elements] Foundation |  | A. Foundation - [Supplemental Elements] Foundation | A. Foundation | [Supplemental Elements] Foundation |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | B10 |  | B10 - Superstructure | B10 - Superstructure |  |  | B. Superstructure | B. Superstructure | [5 empty] | General Category |  | 21-02 10 | Superstructure
System | B10 | Not on One-Line | B10 - Superstructure - (System) Building | B10 - Superstructure | (System) Building |  | B. Superstructure - (System) Building | B. Superstructure | (System) Building |  | SYS Building | Each building | No barcode - Track by location | Generic representation of the building |  | 21-02 10 | Superstructure |  |  | 23-19 29 00 | Complete Buildings
System | B10 | Not on One-Line | B10 - Superstructure - (System) Parking Structure | B10 - Superstructure | (System) Parking Structure |  | B. Superstructure - (System) Parking Structure | B. Superstructure | (System) Parking Structure |  | SYS Parking | Each Complete Structure | No barcode - Track by location | Generic representation of a parking garage or a parking lot. |  | 21-07 20 20 | Parking Lots | 22-01 55 00 | Vehicular Access and Parking | 23-11 23 00 | Parking Controls
Asset | B1080.10 | B10/C10-1 | B10 - Superstructure - Convenience Stair | B10 - Superstructure | Convenience Stair |  | B. Superstructure - Convenience Stair | B. Superstructure | Convenience Stair |  | Convenience Stair | Each convenience stair | No barcode - Track by location | A stairway between floors that is not fire rated and used for ease of movement between floors. Typically found in lobbies or where different elevations are required. |  | 21-02 10 80 | Stairs |  |  | 23-17 23 17 | Stairs
Asset | B1080.10 | B10/C10-1 | B10 - Superstructure - Egress Stair | B10 - Superstructure | Egress Stair |  | B. Superstructure - Egress Stair | B. Superstructure | Egress Stair |  | Egress Stair | Each egress stair | No barcode - Track by location | A fire-rated stairwell used to move occupants from the building to a fire-rated corridor or to the exterior of the building. |  | 21-02 10 80 | Stairs |  |  | 23-17 23 19 11 | Escape Ladders, Stairs | 13-23 11 13 11 | Egress Stairway
Asset | B1080.60 | Not on One-Line | B10 - Superstructure - Fire Escape | B10 - Superstructure | Fire Escape |  | B. Superstructure - Fire Escape | B. Superstructure | Fire Escape |  | Fire Escape | Each fire escape | No barcode - Track by location | A metal staircase on the outside of a building, which can be used to escape from the building if there is a fire. |  | 21-02 10 80 60 | Fire Escapes | 22-05 51 23 | Metal Fire Escapes | 23-17 23 19 11 11 | Fire Escapes
Asset | B1080.80 | Not on One-Line | B10 - Superstructure - Ladder | B10 - Superstructure | Ladder |  | B. Superstructure - Ladder | B. Superstructure | Ladder |  | Ladder | Each ladder | No barcode - Track by location | A fixed ladder to the building structure that is used to access roofs or other areas that are not accessible by elevators or stairways. |  | 21-02 10 80 60 | Fire Escapes | 22-05 51 33 | Metal Ladders | 23-17 23 19 11 | Escape Ladders, Stairs
Supplemental Elements | B1090.99 | n/a | B10 - Superstructure - [Supplemental Elements] Building | B10 - Superstructure | [Supplemental Elements] Building |  | B. Superstructure - [Supplemental Elements] Building | B. Superstructure | [Supplemental Elements] Building |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Supplemental Elements | B1090.99 | n/a | B10 - Superstructure - [Supplemental Elements] Parking Garage | B10 - Superstructure | [Supplemental Elements] Parking Garage |  | B. Superstructure - [Supplemental Elements] Parking Garage | B. Superstructure | [Supplemental Elements] Parking Garage |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | B20 |  | B20 - Vertical Enclosures | B20 - Vertical Enclosures |  |  | B. Vertical Enclosures | B. Vertical Enclosures | [5 empty] | General Category |  | 21-02 20 | Exterior Vertical Enclosures
System | B20 | Not on One-Line | B20 - Vertical Enclosures - (System) Façades and Windows | B20 - Vertical Enclosures | (System) Façades and Windows |  | B. Vertical Enclosures - (System) Façades and Windows | B. Vertical Enclosures | (System) Façades and Windows |  | SYS Facades/Windows ([Façade Description]) | Each building, possibly segmented by Façade | No barcode - Track by location | Generic representation of the building's facades |  | 21-02 10 | Superstructure |  |  | 23-19 29 00 | Complete Buildings
Asset | B2010 | B10/C10-1 | B20 - Vertical Enclosures - Exterior Wall | B20 - Vertical Enclosures | Exterior Wall |  | B. Vertical Enclosures - Exterior Wall | B. Vertical Enclosures | Exterior Wall |  | Exterior Wall | Entire system or geo orientation | No barcode - Track by system | The building envelope providing physical isolation between the interior and the outside environment. Materials and means of construction vary widely. |  | 21-02 20 10 | Exterior Walls |  |  | 23-13 33 15 | Wall Exteriors
Asset | B2020 | Not on One-Line | B20 - Vertical Enclosures - Exterior Window | B20 - Vertical Enclosures | Exterior Window |  | B. Vertical Enclosures - Exterior Window | B. Vertical Enclosures | Exterior Window |  | Exterior Window | Entire system or geo orientation | No barcode - Track by system | Penetrations to allow light to enter, ventilation or visual contact with the exterior. |  | 21-02 20 20 | Exterior Windows | 22-08 50 00 | Windows | 23-17 13 00 | Windows
Asset | B2050 | Not on One-Line | B20 - Vertical Enclosures - Exterior Door | B20 - Vertical Enclosures | Exterior Door |  | B. Vertical Enclosures - Exterior Door | B. Vertical Enclosures | Exterior Door |  | Exterior Door | Each door assembly | Inside of door frame, 6" below upper hinge (or above UL label) | A door, normally weatherproof, that is mounted on the exterior of a building. |  | 21-02 20 50 | Exterior Doors and Grilles |  |  | 23-13 33 21 | Entrances
Asset | B2050.10 | Not on One-Line | B20 - Vertical Enclosures - Exterior Revolving Door | B20 - Vertical Enclosures | Exterior Revolving Door |  | B. Vertical Enclosures - Exterior Revolving Door | B. Vertical Enclosures | Exterior Revolving Door |  | Exterior Revolving Door | Each door assembly | Inside on door assembly | An entrance door for excluding drafts from the interior of a building, usually consisting of four rigid leaves set in the form of a cross and rotating about a central, vertical pivot in the doorway. |  | 21-02 20 50 10 | Exterior Entrance Doors | 22-08 42 33 | Revolving Door Entrances | 23-13 33 21 11 13 | Revolving Door Aluminum-Framed Entrances
Asset | B2050.30 | Not on One-Line | B20 - Vertical Enclosures - Overhead Door | B20 - Vertical Enclosures | Overhead Door |  | B. Vertical Enclosures - Overhead Door | B. Vertical Enclosures | Overhead Door |  | Overhead Door | Each door assembly | On Frame | A door that lifts vertically on tracks to rotate on the same tracks to a horizontal position. Normally provided with springs to make lifting the door easier. |  | 21-03 10 30 | Interior Doors | 22-08 31 00 | Access Doors and Panels
Asset | B2050.70 | Not on One-Line | B20 - Vertical Enclosures - Exterior Gate | B20 - Vertical Enclosures | Exterior Gate |  | B. Vertical Enclosures - Exterior Gate | B. Vertical Enclosures | Exterior Gate |  | Exterior Gate | Each door assembly | Inside on door assembly | A gate used either to limit access to exterior building areas or section of a property or campus. |  | 21-02 20 50 70 | Exterior Gates |  |  | 23-11 25 15 | Perimeter Gates
Asset | B2050.90 | Not on One-Line | B20 - Vertical Enclosures - Door Grate | B20 - Vertical Enclosures | Door Grate |  | B. Vertical Enclosures - Door Grate | B. Vertical Enclosures | Door Grate |  | Door Grate | Each assembly | Upper left of frame on hinge side | A barrier typically hinged that swings across the door opening and utilized to limit access when the door is open. Allows air movement and visual communication. May take the form of a half door (Dutch door). |  | 21-03 10 30 90 | Interior Door Supplementary Components | 22-08 10 00 | Doors and Frames
Asset | B2070 | Not on One-Line | B20 - Vertical Enclosures - Exterior Louvers and Vents | B20 - Vertical Enclosures | Exterior Louvers and Vents |  | B. Vertical Enclosures - Exterior Louvers and Vents | B. Vertical Enclosures | Exterior Louvers and Vents |  | Exterior Louvers and Vents | Each louver or vent | No barcode - Track by system | Penetrations in the building envelop designed to allow air movement into or out of the building. Designed to prevent entry of rain, birds and rodents. |  | 21-02 20 70 | Exterior Louvers and Vents | 22-08 90 00 | Louvers and Vents | 23-17 21 11 15 | Exterior Louvers and Grilles
Asset | B2080.50 | Not on One-Line | B20 - Vertical Enclosures - Exterior Balcony Railings | B20 - Vertical Enclosures | Exterior Balcony Railings |  | B. Vertical Enclosures - Exterior Balcony Railings | B. Vertical Enclosures | Exterior Balcony Railings |  | Exterior Balcony Railings | Each balcony | No barcode - Track by location | The fall protection surrounding a balustraded or railed elevated platform projecting from the wall of a building. |  | 21-02 20 80 50 | Exterior Balcony Walls and Railings | 22-05 52 00 | Metal Railings | 23-13 35 23 17 | Balconies and Overhang Units
Supplemental Elements | B2090.99 | n/a | B20 - Vertical Enclosures - [Supplemental Elements] Façades and Windows | B20 - Vertical Enclosures | [Supplemental Elements] Façades and Windows |  | B. Vertical Enclosures - [Supplemental Elements] Façades and Windows | B. Vertical Enclosures | [Supplemental Elements] Façades and Windows |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | B30 |  | B30 - Roof | B30 - Roof |  |  | B. Roof | B. Roof | [5 empty] | General Category |  | 21-02 30 | Exterior Horizontal Enclosures
System | B30 | Not on One-Line | B30 - Roof - (System) Roof | B30 - Roof | (System) Roof |  | B. Roof - (System) Roof | B. Roof | (System) Roof |  | SYS Roofs | Each building, possibly segmented by roof. | No barcode - Track by location | Generic representation of the building's horizontal enclosure. |  | 21-02 10 | Superstructure |  |  | 23-19 29 00 | Complete Buildings
Asset | B3010 | B10/C10-1 | B30 - Roof - Roof | B30 - Roof | Roof |  | B. Roof - Roof | B. Roof | Roof |  | Roof | Each roof | No barcode - Track by building & floor level | Roofing system, openings, hatches, drain, gutters and downspouts, and gravity ventilators. |  | 21-02 30 10 | Roofing | 22-07 72 00 | Roof Accessories | 23-13 39 00 | Roof Coverings, Claddings, Linings
Asset | B3040 | Not on One-Line | B30 - Roof - Traffic Bearing Horizontal Enclosure | B30 - Roof | Traffic Bearing Horizontal Enclosure |  | B. Roof - Traffic Bearing Horizontal Enclosure | B. Roof | Traffic Bearing Horizontal Enclosure |  | Traffic Bearing Horizontal Enclosure | Each roof | No barcode - Track by building & floor level | A roof on a facility that is designed for parking cars. |  | 21-02 30 40 | Traffic Bearing Horizontal Enclosures | 22-07 72 46 | Roof Walkways | 23-13 41 19 | Roof Walkways
Asset | B3060.10 | Not on One-Line | B30 - Roof - Roof Windows and Skylights | B30 - Roof | Roof Windows and Skylights |  | B. Roof - Roof Windows and Skylights | B. Roof | Roof Windows and Skylights |  | Roof Windows and Skylights | Entire group | No barcode - Track by system | An element of the roof construction that allows light to enter. Modern systems typically are sealed. |  | 21-02 30 60 10 | Roof Windows and Skylights | 22-08 60 00 | Roof Windows and Skylights | 23-17 17 00 | Skylights
Supplemental Elements | B3090.99 | n/a | B30 - Roof - [Supplemental Elements] Roof | B30 - Roof | [Supplemental Elements] Roof |  | B. Roof - [Supplemental Elements] Roof | B. Roof | [Supplemental Elements] Roof |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | C1000a |  | C1000a - Rooms | C1000a - Rooms |  |  | C. Interiors - Rooms | C. Interiors - Rooms | [5 empty] | General Category
System | C1000a | Not on One-Line | C1000a - Rooms - (System) Room without Env. Controls | C1000a - Rooms | (System) Room without Env. Controls |  | C. Interiors - Rooms - (System) Room without Env. Controls | C. Interiors - Rooms | (System) Room without Env. Controls |  | SYS Rooms | Generic asset | As needed | Generic representation of any room
Space | C1000a | Not on One-Line | C1000a - Rooms - Electrical | C1000a - Rooms | Electrical |  | C. Interiors - Rooms - Electrical | C. Interiors - Rooms | Electrical |  | Electrical [Room / Closet] | Each room | Door Frame, Outside, Upper frame corner, above hinges | A room located on a floor of a building that contains electrical distribution equipment including but not limited to distribution panels, transformers, 480/277 electrical panels, 120/208 electrical panels, bus ducts and or bus duct switches. The room has a 2 hour fire rating. |  | 21-07 40 10 10 | Electrical Utility Services | 22-33 71 73 |  | 23-19 31 15 | Special Purpose Rooms | 13-23 19 27 | Electrical Room
Space | C1000a | Not on One-Line | C1000a - Rooms - Electrical Vault | C1000a - Rooms | Electrical Vault |  | C. Interiors - Rooms - Electrical Vault | C. Interiors - Rooms | Electrical Vault |  | Electrical Vault | Each room | Door Frame, Outside, Upper frame corner, above hinges | A fire-rated room, either within the facility or underground, that contains the primary electrical service to a facility. These vaults are commonly constructed out of reinforced concrete boxes, poured concrete or brick. In many cases these vaults are owned by the utility company and they need to be present in order to get access. |  | 21-07 40 10 10 | Electrical Utility Services | 22-33 71 73 |  | 23-19 31 15 | Special Purpose Rooms | 13-23 19 33 | Transformer Vault
Space | C1000a | Not on One-Line | C1000a - Rooms - Elevator Machine Room | C1000a - Rooms | Elevator Machine Room |  | C. Interiors - Rooms - Elevator Machine Room | C. Interiors - Rooms | Elevator Machine Room |  | Elevator Machine Room | Each room | Door Frame, Outside, Upper frame corner, above hinges | A room that houses elevator drives and controllers (sometimes known as elevator machinery room or lift motor room). | [5 empty] | 23-19 31 15 | Special Purpose Rooms | 13-23 11 11 17 | Elevator Machine Room
Space | C1000a | Not on One-Line | C1000a - Rooms - Emergency Generator Room | C1000a - Rooms | Emergency Generator Room |  | C. Interiors - Rooms - Emergency Generator Room | C. Interiors - Rooms | Emergency Generator Room |  | Emergency Generator Room | Each room | Door Frame, Outside, Upper frame corner, above hinges | A two hour fire-rated room that houses the emergency power generator(s) that is dedicated for the sole purpose of housing the emergency power generator. No other equipment, except that which serves the space is permitted in the room. Room must have a door with a 1½ hour fire rating, with a closure and positive latching hardware. Any ductwork that penetrates the fire-rated walls must have a fire damper rated for at least 1½ hours. All penetrations through the walls must be properly sealed with fire-rated materials. | [5 empty] | 23-19 31 15 | Special Purpose Rooms | 13-23 19 27 | Electrical Room
Space | C1000a | Not on One-Line | C1000a - Rooms - Fire Command Center | C1000a - Rooms | Fire Command Center |  | C. Interiors - Rooms - Fire Command Center | C. Interiors - Rooms | Fire Command Center |  | Fire Command Center | Each room | Door Frame, Outside, Upper frame corner, above hinges | A space utilized for management of management primarily of fire related incidents. Fire alarms and communications equipment are provided. May be a dedicated room or a shared area. | [5 empty] | 23-19 31 15 | Special Purpose Rooms | 13-51 44 53 | Recovery Room, Surgical
Space | C1000a | Not on One-Line | C1000a - Rooms - Mechanical | C1000a - Rooms | Mechanical |  | C. Interiors - Rooms - Mechanical | C. Interiors - Rooms | Mechanical |  | Mechanical Equipment [Room/Closet] | Each room | Door Frame, Outside, Upper frame corner, above hinges | A room or space in a building dedicated to the mechanical equipment and its associated electrical equipment, as opposed to rooms intended for human occupancy or storage. | [5 empty] | 23-19 31 15 | Special Purpose Rooms | 13-23 19 00 | Utility Equipment Room
Supplemental Elements | C1000a.99 | n/a | C1000a - Rooms - [Supplemental Elements] Room | C1000a - Rooms | [Supplemental Elements] Room |  | C. Interiors - Rooms - [Supplemental Elements] Room | C. Interiors - Rooms | [Supplemental Elements] Room |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | C1000b |  | C1000b - Rooms with Env. Controls | C1000b - Rooms with Env. Controls |  |  | C. Interiors - Env Contr Rooms | C. Interiors - Env Contr Rooms | [5 empty] | General Category | [5 empty] | 23-27 11 13 23 | Pressure Sensors | 13-51 44 00 | Surgical Spaces
System | C1000b | Not on One-Line | C1000b - Rooms with Env. Controls - (System) Env Contr Rooms | C1000b - Rooms with Env. Controls | (System) Env Contr Rooms |  | C. Interiors - Env Contr Rooms - (System) Env Contr Rooms | C. Interiors - Env Contr Rooms | (System) Env Contr Rooms |  | SYS Env Contr Rooms | Generic asset | As needed | Generic representation of rooms that have air pressure and other climate control requirements.
Space | C1000b | Not on One-Line | C1000b - Rooms with Env. Controls - Negative | C1000b - Rooms with Env. Controls | Negative |  | C. Interiors - Env Contr Rooms - Negative | C. Interiors - Env Contr Rooms | Negative |  | Env Contr. Room - Negative air pressure | Each room | Door Frame, Outside, Upper frame corner, above hinges | This category is set up as an alternative to the detailed categories below.
Space | C1000b | Not on One-Line | C1000b - Rooms with Env. Controls - Positive | C1000b - Rooms with Env. Controls | Positive |  | C. Interiors - Env Contr Rooms - Positive | C. Interiors - Env Contr Rooms | Positive |  | Env Contr. Room - Positive air pressure | Each room | Door Frame, Outside, Upper frame corner, above hinges | This category is set up as an alternative to the detailed categories below.
Supplemental Elements | C1000b.99 | n/a | C1000b - Rooms with Env. Controls - [Supplemental Elements] Env Contr Rooms | C1000b - Rooms with Env. Controls | [Supplemental Elements] Env Contr Rooms |  | C. Interiors - Env Contr Rooms - [Supplemental Elements] Env Contr Rooms | C. Interiors - Env Contr Rooms | [Supplemental Elements] Env Contr Rooms |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | C1000c |  | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care |  |  | C. Interiors - Env Contr Rooms, Patient Care | C. Interiors - Env Contr Rooms, Patient Care | [5 empty] | General Category | [5 empty] | 23-27 11 13 23 | Pressure Sensors | 13-51 44 00 | Surgical Spaces
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Airborne infection isolation (AII) Anteroom | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Airborne infection isolation (AII) Anteroom |  | C. Interiors - Env Contr Rooms, Patient Care - Airborne infection isolation (AII) Anteroom | C. Interiors - Env Contr Rooms, Patient Care | Airborne infection isolation (AII) Anteroom |  | Airborne infection isolation (AII) anteroom | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.4.2.3 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 11 | Anteroom, Inpatient Airborne Infection Isolation
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Airborne Infection Isolation (AII) Room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Airborne Infection Isolation (AII) Room |  | C. Interiors - Env Contr Rooms, Patient Care - Airborne Infection Isolation (AII) Room | C. Interiors - Env Contr Rooms, Patient Care | Airborne Infection Isolation (AII) Room |  | Airborne Infection Isolation (AII) room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.4.2 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 35 11 | Patient Room, Airborne Infection Isolation
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Caesarean Delivery room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Caesarean Delivery room |  | C. Interiors - Env Contr Rooms, Patient Care - Caesarean Delivery room | C. Interiors - Env Contr Rooms, Patient Care | Caesarean Delivery room |  | Caesarean Delivery room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.11.9 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 44 17 | Cesarean Birth Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Combination AII/PE Anteroom | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Combination AII/PE Anteroom |  | C. Interiors - Env Contr Rooms, Patient Care - Combination AII/PE Anteroom | C. Interiors - Env Contr Rooms, Patient Care | Combination AII/PE Anteroom |  | Combination AII/PE Anteroom | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.2.4.5 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 11 | Anteroom, Inpatient Airborne Infection Isolation
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Combination AII/PE Room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Combination AII/PE Room |  | C. Interiors - Env Contr Rooms, Patient Care - Combination AII/PE Room | C. Interiors - Env Contr Rooms, Patient Care | Combination AII/PE Room |  | Combination AII/PE Room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.2.4.5 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 35 11 | Patient Room, Airborne Infection Isolation
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Continued care nursery | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Continued care nursery |  | C. Interiors - Env Contr Rooms, Patient Care - Continued care nursery | C. Interiors - Env Contr Rooms, Patient Care | Continued care nursery |  | Continued care nursery | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.12.3.3 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Critical care patient care station | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Critical care patient care station |  | C. Interiors - Env Contr Rooms, Patient Care - Critical care patient care station | C. Interiors - Env Contr Rooms, Patient Care | Critical care patient care station |  | Critical care patient care station | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.6.1 (formerly Critical and intensive care) |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 35 15 | Patient Room, Intensive Care
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - ED exam/treatment room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | ED exam/treatment room |  | C. Interiors - Env Contr Rooms, Patient Care - ED exam/treatment room | C. Interiors - Env Contr Rooms, Patient Care | ED exam/treatment room |  | ED exam/treatment room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.1.3.6 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - ED human decontamination | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | ED human decontamination |  | C. Interiors - Env Contr Rooms, Patient Care - ED human decontamination | C. Interiors - Env Contr Rooms, Patient Care | ED human decontamination |  | ED human decontamination | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.1.3.6 (8) |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 57 29 | Ethylene Oxide Gas Sterilizer Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - ED trauma/resuscitation room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | ED trauma/resuscitation room |  | C. Interiors - Env Contr Rooms, Patient Care - ED trauma/resuscitation room | C. Interiors - Env Contr Rooms, Patient Care | ED trauma/resuscitation room |  | ED trauma/resuscitation room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.1.3.3 [6] | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 17 23 17 | Nurse Triage Space
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Emergency service triage area | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Emergency service triage area |  | C. Interiors - Env Contr Rooms, Patient Care - Emergency service triage area | C. Interiors - Env Contr Rooms, Patient Care | Emergency service triage area |  | Emergency service triage area | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.1.3.3 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 17 23 17 | Nurse Triage Space
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - ER public waiting area | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | ER public waiting area |  | C. Interiors - Env Contr Rooms, Patient Care - ER public waiting area | C. Interiors - Env Contr Rooms, Patient Care | ER public waiting area |  | ER public waiting area | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.1.3.4 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-55 29 23 13 | Waiting Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Intermediate care patient room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Intermediate care patient room |  | C. Interiors - Env Contr Rooms, Patient Care - Intermediate care patient room | C. Interiors - Env Contr Rooms, Patient Care | Intermediate care patient room |  | Intermediate care patient room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.5.2) | [5 empty] | 23-19 31 19 | Controlled Environment Rooms
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Labor/delivery/recovery (LDR) room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Labor/delivery/recovery (LDR) room |  | C. Interiors - Env Contr Rooms, Patient Care - Labor/delivery/recovery (LDR) room | C. Interiors - Env Contr Rooms, Patient Care | Labor/delivery/recovery (LDR) room |  | Labor/delivery/recovery (LDR) room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.11.3
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Labor/delivery/recovery/postpartum (LDRP) room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Labor/delivery/recovery/postpartum (LDRP) room |  | C. Interiors - Env Contr Rooms, Patient Care - Labor/delivery/recovery/postpartum (LDRP) room | C. Interiors - Env Contr Rooms, Patient Care | Labor/delivery/recovery/postpartum (LDRP) room |  | Labor/delivery/recovery/postpartum (LDRP) room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.11.3
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Laser eye room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Laser eye room |  | C. Interiors - Env Contr Rooms, Patient Care - Laser eye room | C. Interiors - Env Contr Rooms, Patient Care | Laser eye room |  | Laser eye room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 37 29 | Laser Treatment Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Medical/anesthesia gas storage | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Medical/anesthesia gas storage |  | C. Interiors - Env Contr Rooms, Patient Care - Medical/anesthesia gas storage | C. Interiors - Env Contr Rooms, Patient Care | Medical/anesthesia gas storage |  | Medical/anesthesia gas storage | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.3.6.11 [3] |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 44 11 | Anesthesia Workroom and Equipment Storage
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Neonatal intensive care | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Neonatal intensive care |  | C. Interiors - Env Contr Rooms, Patient Care - Neonatal intensive care | C. Interiors - Env Contr Rooms, Patient Care | Neonatal intensive care |  | Neonatal intensive care | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.10.2 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Newborn nursery | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Newborn nursery |  | C. Interiors - Env Contr Rooms, Patient Care - Newborn nursery | C. Interiors - Env Contr Rooms, Patient Care | Newborn nursery |  | Newborn nursery | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.12.3.1
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Nourishment area or room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Nourishment area or room |  | C. Interiors - Env Contr Rooms, Patient Care - Nourishment area or room | C. Interiors - Env Contr Rooms, Patient Care | Nourishment area or room |  | Nourishment area or room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.6.7
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Nursery workroom | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Nursery workroom |  | C. Interiors - Env Contr Rooms, Patient Care - Nursery workroom | C. Interiors - Env Contr Rooms, Patient Care | Nursery workroom |  | Nursery workroom | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.12.6.3
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Operating room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Operating room |  | C. Interiors - Env Contr Rooms, Patient Care - Operating room | C. Interiors - Env Contr Rooms, Patient Care | Operating room |  | Operating room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.3.2 |  |  |  | 22-11 76 00 |  | 23-19 31 19 | Controlled Environment Rooms | 13-51 44 25 | General Operating Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Operating/surgical Cystoscopic room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Operating/surgical Cystoscopic room |  | C. Interiors - Env Contr Rooms, Patient Care - Operating/surgical Cystoscopic room | C. Interiors - Env Contr Rooms, Patient Care | Operating/surgical Cystoscopic room |  | Operating/surgical Cystoscopic room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-11 76 00 |  | 23-19 31 19 | Controlled Environment Rooms | 13-51 21 19 | Cystoscopic Radiology Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Patient care area corridor | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Patient care area corridor |  | C. Interiors - Env Contr Rooms, Patient Care - Patient care area corridor | C. Interiors - Env Contr Rooms, Patient Care | Patient care area corridor |  | Patient care area corridor | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Patient room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Patient room |  | C. Interiors - Env Contr Rooms, Patient Care - Patient room | C. Interiors - Env Contr Rooms, Patient Care | Patient room |  | Patient room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.2.4.5 | [5 empty] | 23-19 31 15 | Special Purpose Rooms | 13-51 14 35 | Patient Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Patient toilet room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Patient toilet room |  | C. Interiors - Env Contr Rooms, Patient Care - Patient toilet room | C. Interiors - Env Contr Rooms, Patient Care | Patient toilet room |  | Toilet, Patient | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.2.6
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Phase I PACU and Phase II recovery | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Phase I PACU and Phase II recovery |  | C. Interiors - Env Contr Rooms, Patient Care - Phase I PACU and Phase II recovery | C. Interiors - Env Contr Rooms, Patient Care | Phase I PACU and Phase II recovery |  | Phase I PACU and Phase II recovery | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.3.4.3 and 2.2-3.3.4.4 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 44 43 | Procedure/Minor Operating Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Procedure Room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Procedure Room |  | C. Interiors - Env Contr Rooms, Patient Care - Procedure Room | C. Interiors - Env Contr Rooms, Patient Care | Procedure Room |  | Procedure Room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 3.7-3.2 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 23 | Corridor Units | 13-25 11 11 | Corridor
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Protective Environment (PE) anteroom | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Protective Environment (PE) anteroom |  | C. Interiors - Env Contr Rooms, Patient Care - Protective Environment (PE) anteroom | C. Interiors - Env Contr Rooms, Patient Care | Protective Environment (PE) anteroom |  | Protective Environment (PE) anteroom | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Protective Environment (PE) room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Protective Environment (PE) room |  | C. Interiors - Env Contr Rooms, Patient Care - Protective Environment (PE) room | C. Interiors - Env Contr Rooms, Patient Care | Protective Environment (PE) room |  | Protective Environment (PE) room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-2.2.4.4 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 35 27 | Patient Room, Protective Environment Isolation
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Radiology waiting room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Radiology waiting room |  | C. Interiors - Env Contr Rooms, Patient Care - Radiology waiting room | C. Interiors - Env Contr Rooms, Patient Care | Radiology waiting room |  | Radiology waiting room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-11 77 00 |  | 23-19 31 19 | Controlled Environment Rooms | 13-55 29 23 13 | Waiting Room
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Seclusion room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Seclusion room |  | C. Interiors - Env Contr Rooms, Patient Care - Seclusion room | C. Interiors - Env Contr Rooms, Patient Care | Seclusion room |  | Seclusion room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.4.3 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Sterile processing room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Sterile processing room |  | C. Interiors - Env Contr Rooms, Patient Care - Sterile processing room | C. Interiors - Env Contr Rooms, Patient Care | Sterile processing room |  | Sterile processing room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.3.6.13 (formerly substerile service area) | [5 empty] | 23-19 31 19 | Controlled Environment Rooms
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Treatment room | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Treatment room |  | C. Interiors - Env Contr Rooms, Patient Care - Treatment room | C. Interiors - Env Contr Rooms, Patient Care | Treatment room |  | Treatment room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 17 23 17 | Nurse Triage Space
Space | C1000c | Not on One-Line | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care - Wound intensive care (burn unit) | C1000c - Rooms with Env. Controls, Nursing/Other Patient Care | Wound intensive care (burn unit) |  | C. Interiors - Env Contr Rooms, Patient Care - Wound intensive care (burn unit) | C. Interiors - Env Contr Rooms, Patient Care | Wound intensive care (burn unit) |  | Wound intensive care (burn unit) | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 17 23 17 | Nurse Triage Space
Grouping | C1000d |  | C1000d - Rooms with Env. Control, Support Nursing/Other Patient Care | C1000d - Rooms with Env. Control, Support Nursing/Other Patient Care |  |  | C. Interiors - Env Contr Rooms, Patient Care Support | C. Interiors - Env Contr Rooms, Patient Care Support | [5 empty] | General Category
Space | C1000d | Not on One-Line | C1000d - Rooms with Env. Control, Support Nursing/Other Patient Care - Clean supply room | C1000d - Rooms with Env. Control, Support Nursing/Other Patient Care | Clean supply room |  | C. Interiors - Env Contr Rooms, Patient Care Support - Clean supply room | C. Interiors - Env Contr Rooms, Patient Care Support | Clean supply room |  | Clean supply room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.6.9.2 | [5 empty] | 23-19 31 17 11 | Bathroom Units | 13-65 13 00 | Bathroom
Space | C1000d | Not on One-Line | C1000d - Rooms with Env. Control, Support Nursing/Other Patient Care - Clean workroom | C1000d - Rooms with Env. Control, Support Nursing/Other Patient Care | Clean workroom |  | C. Interiors - Env Contr Rooms, Patient Care Support - Clean workroom | C. Interiors - Env Contr Rooms, Patient Care Support | Clean workroom |  | Clean workroom | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.6.9.1 | [5 empty] | 23-19 31 17 | Sanitary Room Units | 23-19 31 17 | Sanitary Room Units
Space | C1000d | Not on One-Line | C1000d - Rooms with Env. Control, Support Nursing/Other Patient Care - Soiled workroom or soiled holding | C1000d - Rooms with Env. Control, Support Nursing/Other Patient Care | Soiled workroom or soiled holding |  | C. Interiors - Env Contr Rooms, Patient Care Support - Soiled workroom or soiled holding | C. Interiors - Env Contr Rooms, Patient Care Support | Soiled workroom or soiled holding |  | Soiled workroom or soiled holding | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-2.6.10 | [5 empty] | 23-19 31 17 | Sanitary Room Units | 13-51 17 11 | Clean Linen Storage Room, Healthcare
Grouping | C1000e |  | C1000e - Rooms with Env. Control, D&T | C1000e - Rooms with Env. Control, D&T |  |  | C. Interiors - Env Contr Rooms, D&T | C. Interiors - Env Contr Rooms, D&T | [5 empty] | General Category |  |  |  | 22-13 49 00 | Radiation Protection
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Bronchoscopy sputum collection and pentamidine admin | C1000e - Rooms with Env. Control, D&T | Bronchoscopy sputum collection and pentamidine admin |  | C. Interiors - Env Contr Rooms, D&T - Bronchoscopy sputum collection and pentamidine admin | C. Interiors - Env Contr Rooms, D&T | Bronchoscopy sputum collection and pentamidine admin |  | Bronchoscopy sputum collection and pentamidine admin | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Dark room | C1000e - Rooms with Env. Control, D&T | Dark room |  | C. Interiors - Env Contr Rooms, D&T - Dark room | C. Interiors - Env Contr Rooms, D&T | Dark room |  | Dark room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.6.6 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Dialysis treatment area | C1000e - Rooms with Env. Control, D&T | Dialysis treatment area |  | C. Interiors - Env Contr Rooms, D&T - Dialysis treatment area | C. Interiors - Env Contr Rooms, D&T | Dialysis treatment area |  | Dialysis treatment area | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Dialyzer reprocessing room | C1000e - Rooms with Env. Control, D&T | Dialyzer reprocessing room |  | C. Interiors - Env Contr Rooms, D&T - Dialyzer reprocessing room | C. Interiors - Env Contr Rooms, D&T | Dialyzer reprocessing room |  | Dialyzer reprocessing room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - ECT procedure room | C1000e - Rooms with Env. Control, D&T | ECT procedure room |  | C. Interiors - Env Contr Rooms, D&T - ECT procedure room | C. Interiors - Env Contr Rooms, D&T | ECT procedure room |  | ECT procedure room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.5-3.4.2.2 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Endoscope cleaning | C1000e - Rooms with Env. Control, D&T | Endoscope cleaning |  | C. Interiors - Env Contr Rooms, D&T - Endoscope cleaning | C. Interiors - Env Contr Rooms, D&T | Endoscope cleaning |  | Endoscope cleaning | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Gastrointestinal endoscopy procedure room | C1000e - Rooms with Env. Control, D&T | Gastrointestinal endoscopy procedure room |  | C. Interiors - Env Contr Rooms, D&T - Gastrointestinal endoscopy procedure room | C. Interiors - Env Contr Rooms, D&T | Gastrointestinal endoscopy procedure room |  | Gastrointestinal endoscopy procedure room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Hydrotherapy | C1000e - Rooms with Env. Control, D&T | Hydrotherapy |  | C. Interiors - Env Contr Rooms, D&T - Hydrotherapy | C. Interiors - Env Contr Rooms, D&T | Hydrotherapy |  | Hydrotherapy | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Imaging (D&T) | C1000e - Rooms with Env. Control, D&T | Imaging (D&T) |  | C. Interiors - Env Contr Rooms, D&T - Imaging (D&T) | C. Interiors - Env Contr Rooms, D&T | Imaging (D&T) |  | Imaging (D&T) | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P (formerly X-ray (D&T) |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Interventional and intraoperative MRI procedure room | C1000e - Rooms with Env. Control, D&T | Interventional and intraoperative MRI procedure room |  | C. Interiors - Env Contr Rooms, D&T - Interventional and intraoperative MRI procedure room | C. Interiors - Env Contr Rooms, D&T | Interventional and intraoperative MRI procedure room |  | Interventional and intraoperative MRI procedure room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.5.2 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Interventional imaging procedure room | C1000e - Rooms with Env. Control, D&T | Interventional imaging procedure room |  | C. Interiors - Env Contr Rooms, D&T - Interventional imaging procedure room | C. Interiors - Env Contr Rooms, D&T | Interventional imaging procedure room |  | Interventional imaging procedure room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.5.2 (formerly X-ray Surgery/critical care and catheterization) |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Medication room | C1000e - Rooms with Env. Control, D&T | Medication room |  | C. Interiors - Env Contr Rooms, D&T - Medication room | C. Interiors - Env Contr Rooms, D&T | Medication room |  | Medication room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Nuclear medicine hot lab | C1000e - Rooms with Env. Control, D&T | Nuclear medicine hot lab |  | C. Interiors - Env Contr Rooms, D&T - Nuclear medicine hot lab | C. Interiors - Env Contr Rooms, D&T | Nuclear medicine hot lab |  | Nuclear medicine hot lab | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Nuclear medicine procedure room | C1000e - Rooms with Env. Control, D&T | Nuclear medicine procedure room |  | C. Interiors - Env Contr Rooms, D&T - Nuclear medicine procedure room | C. Interiors - Env Contr Rooms, D&T | Nuclear medicine procedure room |  | Nuclear medicine procedure room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.2-3.6.1 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Physical Therapy Room | C1000e - Rooms with Env. Control, D&T | Physical Therapy Room |  | C. Interiors - Env Contr Rooms, D&T - Physical Therapy Room | C. Interiors - Env Contr Rooms, D&T | Physical Therapy Room |  | Physical Therapy Room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000e | Not on One-Line | C1000e - Rooms with Env. Control, D&T - Special examination room | C1000e - Rooms with Env. Control, D&T | Special examination room |  | C. Interiors - Env Contr Rooms, D&T - Special examination room | C. Interiors - Env Contr Rooms, D&T | Special examination room |  | Special examination room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Grouping | C1000f |  | C1000f - Rooms with Env. Control, Patient Support | C1000f - Rooms with Env. Control, Patient Support |  |  | C. Interiors - Env Contr Rooms, Patient Support | C. Interiors - Env Contr Rooms, Patient Support | [5 empty] | General Category
Space | C1000f | Not on One-Line | C1000f - Rooms with Env. Control, Patient Support - Bedpan room | C1000f - Rooms with Env. Control, Patient Support | Bedpan room |  | C. Interiors - Env Contr Rooms, Patient Support - Bedpan room | C. Interiors - Env Contr Rooms, Patient Support | Bedpan room |  | Bedpan room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000f | Not on One-Line | C1000f - Rooms with Env. Control, Patient Support - Environmental services room | C1000f - Rooms with Env. Control, Patient Support | Environmental services room |  | C. Interiors - Env Contr Rooms, Patient Support - Environmental services room | C. Interiors - Env Contr Rooms, Patient Support | Environmental services room |  | Environmental services room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-4.8.12 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000f | Not on One-Line | C1000f - Rooms with Env. Control, Patient Support - Food and supply storage | C1000f - Rooms with Env. Control, Patient Support | Food and supply storage |  | C. Interiors - Env Contr Rooms, Patient Support - Food and supply storage | C. Interiors - Env Contr Rooms, Patient Support | Food and supply storage |  | Food and supply storage | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-4.3.8.11 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000f | Not on One-Line | C1000f - Rooms with Env. Control, Patient Support - Kitchen | C1000f - Rooms with Env. Control, Patient Support | Kitchen |  | C. Interiors - Env Contr Rooms, Patient Support - Kitchen | C. Interiors - Env Contr Rooms, Patient Support | Kitchen |  | Kitchen | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-4.3.2 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000f | Not on One-Line | C1000f - Rooms with Env. Control, Patient Support - Laboratory work area | C1000f - Rooms with Env. Control, Patient Support | Laboratory work area |  | C. Interiors - Env Contr Rooms, Patient Support - Laboratory work area | C. Interiors - Env Contr Rooms, Patient Support | Laboratory work area |  | Laboratory work area | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - represents multiple categories in ASHRAE 170 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000f | Not on One-Line | C1000f - Rooms with Env. Control, Patient Support - Pharmacy Services: Pharmacy Areas | C1000f - Rooms with Env. Control, Patient Support | Pharmacy Services: Pharmacy Areas |  | C. Interiors - Env Contr Rooms, Patient Support - Pharmacy Services: Pharmacy Areas | C. Interiors - Env Contr Rooms, Patient Support | Pharmacy Services: Pharmacy Areas |  | Pharmacy | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-4.2.2 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000f | Not on One-Line | C1000f - Rooms with Env. Control, Patient Support - Toilet room | C1000f - Rooms with Env. Control, Patient Support | Toilet room |  | C. Interiors - Env Contr Rooms, Patient Support - Toilet room | C. Interiors - Env Contr Rooms, Patient Support | Toilet room |  | Toilet, Patient Support | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-4.3.9.1 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Space | C1000f | Not on One-Line | C1000f - Rooms with Env. Control, Patient Support - Warewashing | C1000f - Rooms with Env. Control, Patient Support | Warewashing |  | C. Interiors - Env Contr Rooms, Patient Support - Warewashing | C. Interiors - Env Contr Rooms, Patient Support | Warewashing |  | Warewashing | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-4.3.4 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Grouping | C1000g |  | C1000g - Rooms with Env. Control, Sterile Processing | C1000g - Rooms with Env. Control, Sterile Processing |  |  | C. Interiors - Env Contr Rooms, Sterile Processing | C. Interiors - Env Contr Rooms, Sterile Processing | [5 empty] | General Category
Space | C1000g | Not on One-Line | C1000g - Rooms with Env. Control, Sterile Processing - Clean assembly/workroom | C1000g - Rooms with Env. Control, Sterile Processing | Clean assembly/workroom |  | C. Interiors - Env Contr Rooms, Sterile Processing - Clean assembly/workroom | C. Interiors - Env Contr Rooms, Sterile Processing | Clean assembly/workroom |  | Sterile Processing Clean workroom | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.1.2 | [5 empty] | 23-19 31 17 | Sanitary Room Units | 13-51 57 31 | Instrument Sterilization Room
Space | C1000g | Not on One-Line | C1000g - Rooms with Env. Control, Sterile Processing - Soiled workroom/decontamination room | C1000g - Rooms with Env. Control, Sterile Processing | Soiled workroom/decontamination room |  | C. Interiors - Env Contr Rooms, Sterile Processing - Soiled workroom/decontamination room | C. Interiors - Env Contr Rooms, Sterile Processing | Soiled workroom/decontamination room |  | Sterile Processing Soiled workroom/decontamination | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.1.3 | [5 empty] | 23-19 31 17 | Sanitary Room Units | 13-51 57 31 | Instrument Sterilization Room
Space | C1000g | Not on One-Line | C1000g - Rooms with Env. Control, Sterile Processing - Sterile storage room | C1000g - Rooms with Env. Control, Sterile Processing | Sterile storage room |  | C. Interiors - Env Contr Rooms, Sterile Processing - Sterile storage room | C. Interiors - Env Contr Rooms, Sterile Processing | Sterile storage room |  | Sterile Processing Sterile storage | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.1.4.1 |  |  |  | 22-13 21 00 | Controlled Environment Rooms | 23-19 31 19 | Controlled Environment Rooms | 13-51 14 13 | Anteroom, Inpatient Protective Environment Isolation
Grouping | C1000h |  | C10g - Rooms with Env. Control, Sterile Processing - Sterile storage room (clean/sterile medical/surgical supplies) | C1000h - Rooms with Env. Control, General Support |  |  | C. Interiors - Env Contr Rooms, General Support | C. Interiors - Env Contr Rooms, General Support | [5 empty] | General Category
Space | C1000h | Not on One-Line | C1000h - Rooms with Env. Control, General Support - Autopsy Room | C1000h - Rooms with Env. Control, General Support | Autopsy Room |  | C. Interiors - Env Contr Rooms, General Support - Autopsy Room | C. Interiors - Env Contr Rooms, General Support | Autopsy Room |  | Autopsy Room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.7.2.2 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 47 73 | Medical Autopsy Room
Space | C1000h | Not on One-Line | C1000h - Rooms with Env. Control, General Support - Clean linen storage room | C1000h - Rooms with Env. Control, General Support | Clean linen storage room |  | C. Interiors - Env Contr Rooms, General Support - Clean linen storage room | C. Interiors - Env Contr Rooms, General Support | Clean linen storage room |  | Clean linen storage room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.2.3.2 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 41 13 | Bronchoscopy Procedure Room
Space | C1000h | Not on One-Line | C1000h - Rooms with Env. Control, General Support - Hazardous material storage | C1000h - Rooms with Env. Control, General Support | Hazardous material storage |  | C. Interiors - Env Contr Rooms, General Support - Hazardous material storage | C. Interiors - Env Contr Rooms, General Support | Hazardous material storage |  | Hazardous material storage | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 44 43 | Procedure/Minor Operating Room
Space | C1000h | Not on One-Line | C1000h - Rooms with Env. Control, General Support - Laundry, processing room | C1000h - Rooms with Env. Control, General Support | Laundry, processing room |  | C. Interiors - Env Contr Rooms, General Support - Laundry, processing room | C. Interiors - Env Contr Rooms, General Support | Laundry, processing room |  | Laundry, processing room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.2.2 [2] | [5 empty] | 23-19 31 19 | Controlled Environment Rooms
Space | C1000h | Not on One-Line | C1000h - Rooms with Env. Control, General Support - Linen and refuse chute room | C1000h - Rooms with Env. Control, General Support | Linen and refuse chute room |  | C. Interiors - Env Contr Rooms, General Support - Linen and refuse chute room | C. Interiors - Env Contr Rooms, General Support | Linen and refuse chute room |  | Linen and refuse chute room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.4.1.4 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 41 15 | Endoscope Clean-up, Sterilization, and Storage Room
Space | C1000h | Not on One-Line | C1000h - Rooms with Env. Control, General Support - Nonrefrigerated body-holding room | C1000h - Rooms with Env. Control, General Support | Nonrefrigerated body-holding room |  | C. Interiors - Env Contr Rooms, General Support - Nonrefrigerated body-holding room | C. Interiors - Env Contr Rooms, General Support | Nonrefrigerated body-holding room |  | Nonrefrigerated body-holding room | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 47 00 | Clinical Laboratory Spaces
Space | C1000h | Not on One-Line | C1000h - Rooms with Env. Control, General Support - Regulated waste holding space | C1000h - Rooms with Env. Control, General Support | Regulated waste holding space |  | C. Interiors - Env Contr Rooms, General Support - Regulated waste holding space | C. Interiors - Env Contr Rooms, General Support | Regulated waste holding space |  | Regulated waste holding space | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.4.1.3 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-51 51 45 | Microbiology Media Preparation Laboratory
Space | C1000h | Not on One-Line | C1000h - Rooms with Env. Control, General Support - Toilet | C1000h - Rooms with Env. Control, General Support | Toilet |  | C. Interiors - Env Contr Rooms, General Support - Toilet | C. Interiors - Env Contr Rooms, General Support | Toilet |  | Toilet, Public | Each room | Door Frame, Outside, Upper frame corner, above hinges | per ASHRAE170:2017 Addendum P - FGI 2.1-5.2.4.1 | [5 empty] | 23-19 31 19 | Controlled Environment Rooms | 13-47 17 13 11 | Morgue Compartment
Grouping | C1010 |  | C1010 - Interiors - Barrier Walls | C1010 - Interiors - Barrier Walls |  |  | C. Interiors - Barrier Walls | C. Interiors - Barrier Walls | [5 empty] | General Category | [5 empty] | 23-15 13 13 | Interior Wall and Ceiling Cladding
System | C1010 | Not on One-Line | C1010 - Interiors - Barrier Walls - (System) Barrier Walls | C1010 - Interiors - Barrier Walls | (System) Barrier Walls |  | C. Interiors - Barrier Walls - (System) Barrier Walls | C. Interiors - Barrier Walls | (System) Barrier Walls |  | SYS Barrier Wall ([Wall Cluster]) | Each building, possibly segmented horizontally by floor or vertically by building geometry. | No barcode - Track by location | Generic representation of barrier walls within system.
Asset | C1010 | B10/C10-1 | C1010 - Interiors - Barrier Walls - Fire Barrier | C1010 - Interiors - Barrier Walls | Fire Barrier |  | C. Interiors - Barrier Walls - Fire Barrier | C. Interiors - Barrier Walls | Fire Barrier |  | Fire Barrier | Each unique barrier or logical major division of barrier | On wall at a visible, easily accessible location near a rating sign if used. Place at a prominent point of barrier section such as by stair or elevator door | These are used for many purposes, including separating occupancies, isolating hazardous areas, creating a horizontal exit, enclosing an exit, or creating a shaft. These barriers have a fire-resistance rating in hours, specified by the code. Depending on the purpose, the fire resistance can be as little as half an hour, or it can be one hour, two hours, and, in some cases, even three hours. Any fire barrier must be complete both horizontally and vertically, the latter meaning that the wall extends from the floor slab through any suspended ceiling and is tight against the floor or roof above. As an option, the barrier can sometimes terminate at the bottom of an interstitial space if the space is designed with a rating equivalent to the fire barrier. All penetrations of the fire barrier must be sealed to maintain the barrier’s fire resistance, and all doors must be fire-protection-rated doors of the appropriate rating. Fire-protection-rated dampers are required in ducts that penetrate fire barriers with a fire resistance greater than one hour. (Source: NFPA.org). If a Fire Barrier is also a Smoke Barrier, use this “Fire Barrier Category” |  | 21-03 10 90 30 | Service Walls | 22-10 25 00 | Service Walls | 23-17 21 15 | Fire and Smoke Shutters and Curtains
Asset | C1010 | B10/C10-1 | C1010 - Interiors - Barrier Walls - Fire Barrier - Horizontal Assembly | C1010 - Interiors - Barrier Walls | Fire Barrier | Horizontal Assembly | C. Interiors - Barrier Walls - Fire Barrier - Horizontal Assembly | C. Interiors - Barrier Walls | Fire Barrier | Horizontal Assembly | Fire Barrier - Horizontal Assembly | Each floor plate | No barcode - Track by location | A fire-resistance-rated floor or roof assembly of materials designed to restrict the spread of fire in which continuity is maintained.
Asset | C1010 | B10/C10-1 | C1010 - Interiors - Barrier Walls - Fire Barrier - Mechanical/Utility Shaft | C1010 - Interiors - Barrier Walls | Fire Barrier | Mechanical/Utility Shaft | C. Interiors - Barrier Walls - Fire Barrier - Mechanical/Utility Shaft | C. Interiors - Barrier Walls | Fire Barrier | Mechanical/Utility Shaft | Fire Barrier - Mechanical/Utility Shaft | Each shaft | No barcode - Track by location | Shaft enclosed by fire barrier that runs through a building vertically and can be treated as one asset. All penetrations to the shaft are fire-rated as well (fire dampers, piping, electrical, telecom, fire stop, etc.).
Asset | C1010 | B10/C10-1 | C1010 - Interiors - Barrier Walls - Smoke Barrier | C1010 - Interiors - Barrier Walls | Smoke Barrier |  | C. Interiors - Barrier Walls - Smoke Barrier | C. Interiors - Barrier Walls | Smoke Barrier |  | Smoke Barrier | Each barrier | Barcode to be placed near barrier label, new label to be placed if barrier turns 90 degrees | These are used to restrict the movement of smoke and usually have a fire-resistance rating specified in the code. In new health care occupancies, the smoke barrier must have a one-hour fire-resistance rating. In existing health care occupancies, the requirement is reduced to a half-hour fire-resistance rating. Any penetrations of the smoke barrier must be sealed to maintain the fire resistance and to ensure that the barrier is relatively smoke-tight. The doors in the smoke barrier may or may not be required to be fire-protection-rated. The code will specify whether such a rating is required. Duct penetrations of smoke barriers will generally require smoke dampers, which are technically called leakage-rated dampers and are operated by smoke detectors. (Source: NFPA.org) If a Smoke Barrier is also a Fire Barrier, use the “Fire Barrier Category” |  | 21-03 10 90 30 | Service Walls | 22-10 25 00 | Service Walls | 23-17 21 15 11 | Fire Shutters
Asset | C1010 | Not on One-Line | C1010 - Interiors - Barrier Walls - Smoke Curtain | C1010 - Interiors - Barrier Walls | Smoke Curtain |  | C. Interiors - Barrier Walls - Smoke Curtain | C. Interiors - Barrier Walls | Smoke Curtain |  | Smoke Curtain | Each unit | On control panel | Smoke curtains and barriers are electrically operated automatic designed to prevent the movement of smoke & heat from one area to another in a fire.
Asset | C1010 | B10/C10-1 | C1010 - Interiors - Barrier Walls - Smoke Partition | C1010 - Interiors - Barrier Walls | Smoke Partition |  | C. Interiors - Barrier Walls - Smoke Partition | C. Interiors - Barrier Walls | Smoke Partition |  | Smoke Partition | Each barrier | Barcode to be placed near barrier label, new label to be placed if barrier turns 90 degrees | Smoke partitions are designed to limit the movement of smoke and are not as substantial as smoke barriers. Smoke partitions generally do not have a fire-resistance rating and may terminate at a suspended ceiling. Walls enclosing a sprinkler-protected hazardous area can constitute smoke partitions. Similarly, the code says that a typical, lay-in acoustical tile ceiling with ducted HVAC can be considered as limiting the transfer of smoke. The doors do not have to be fire-protection-rated, but they must be self-closing. No dampers are required in duct penetrations. (Source: NFPA.org). |  | 21-03 10 90 30 | Service Walls | 22-10 25 00 | Service Walls | 23-17 21 15 15 | Smoke Shutters
Asset | C1010 | Not on One-Line | C1010 - Interiors - Barrier Walls - Suite | C1010 - Interiors - Barrier Walls | Suite |  | C. Interiors - Barrier Walls - Suite | C. Interiors - Barrier Walls | Suite |  | Suite Partition | One asset per Suite | No barcode - Track by suite location (shown on LS drawing) | A smoke rated partition that surrounds a suite. Suites are groups of rooms that for the purposes of life safety, function as one big room. They are limited in size based on whether they are sprinkled, used for patient care, and used for sleeping. (Source: JointCommission.org) There are three different types of Suites: 1) Patient Sleeping; 2) Patient Care; 3) Non-Patient Care |  | 21-03 10 90 30 | Service Walls | 22-10 25 13 | Patient Bed Service Walls | 23-19 31 00 | Room Units
Supplemental Elements | C1010.99 | n/a | C1010 - Interiors - Barrier Walls - [Supplemental Elements] Barrier Walls | C1010 - Interiors - Barrier Walls | [Supplemental Elements] Barrier Walls |  | C. Interiors - Barrier Walls - [Supplemental Elements] Barrier Walls | C. Interiors - Barrier Walls | [Supplemental Elements] Barrier Walls |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | C1030 |  | C1030 - Interiors - Doors | C1030 - Interiors - Doors |  |  | C. Interiors - Doors | C. Interiors - Doors | [5 empty] | General Category |  | 21-03 10 30 | Interior Doors | 22-08 10 00 | Doors and Frames | 23-17 11 00 | Doors
System | C1030 | Not on One-Line | C1030 - Interiors - Doors - (System) Doors | C1030 - Interiors - Doors | (System) Doors |  | C. Interiors - Doors - (System) Doors | C. Interiors - Doors | (System) Doors |  | SYS Doors | Each building, possibly segmented horizontally by floor. | No barcode - Track by location | Generic representation of all interior doors. |  | 21-02 10 | Superstructure |  |  | 23-19 29 00 | Complete Buildings
Asset | C1030.10 | Not on One-Line | C1030 - Interiors - Doors - Corridor Door | C1030 - Interiors - Doors | Corridor Door |  | C. Interiors - Doors - Corridor Door | C. Interiors - Doors | Corridor Door |  | Corridor Door | Each door assembly | Door Frame, 6" below upper hinge (or above UL label), on right top corner if double door, and top door frame, hinge side if single door | A UL door assembly, that separates a room from a corridor, required to be self-latching, so that they do not rebound into a partially open position if forcefully closed. Additionally, it may be door assembly that divides a corridor into multiple sections, not utilized as part of a fire, smoke or fire/smoke barrier. |  | 21-03 10 30 10 | Interior Swinging Doors | 22-08 10 00 | Doors and Frames |  |  | 13-25 11 11 | Corridor
Asset | C1030.10 | B10-1 | C1030 - Interiors - Doors - Fire Door | C1030 - Interiors - Doors | Fire Door |  | C. Interiors - Doors - Fire Door | C. Interiors - Doors | Fire Door |  | Fire Door | Each door assembly | Door Frame, 6" below upper hinge (or above UL label) | A UL rated door assembly, with a rating of 45min and higher, installed to stop the spread of fire. |  | 21-03 10 30 70 | Interior Special Function Doors | 22-08 11 73 | Sliding Metal Fire doors | 23-17 11 31 | Fire Doors
Asset | C1030.10 | Not on One-Line | C1030 - Interiors - Doors - Fire/Smoke Door | C1030 - Interiors - Doors | Fire/Smoke Door |  | C. Interiors - Doors - Fire/Smoke Door | C. Interiors - Doors | Fire/Smoke Door |  | Fire/Smoke Door | Each door assembly | Door Frame, 6" below upper hinge (or above UL label) | A UL rated door assembly, with a rating of 45min and higher, and typically with gaskets, installed to stop the spread of fire and smoke. |  | 21-03 10 30 70 | Interior Special Function Doors | 22-08 11 73 | Sliding Metal Fire doors | 23-17 11 31 | Fire Doors
Asset | C1030.10 | Not on One-Line | C1030 - Interiors - Doors - Smoke Door | C1030 - Interiors - Doors | Smoke Door |  | C. Interiors - Doors - Smoke Door | C. Interiors - Doors | Smoke Door |  | Smoke Door | Each door assembly | Door Frame, 6" below upper hinge (or above UL label) | A UL rated door assembly, often with a 20min rating requirement, typically with gaskets, to stop the spread of smoke in a facility. |  | 21-03 10 30 70 | Interior Special Function Doors | 22-08 10 00 | Doors and Frames
Asset | C1030.25 | Not on One-Line | C1030 - Interiors - Doors - Automatic | C1030 - Interiors - Doors | Automatic |  | C. Interiors - Doors - Automatic | C. Interiors - Doors | Automatic |  | Automatic | Each door assembly | Door Frame, 6" below upper hinge (or above UL label) | Automatic doors use optical or motion detection sensors to activate their motorized opening and closing functions. These sensors are mounted over the automatic door or are integrated into the door framing from above or the side. |  | 21-03 10 30 25 | Interior Sliding Doors | 22-08 11 73 | Sliding Metal Fire doors | 23-17 11 13 19 | Sliding Metal Doors
Asset | C1030.25 | Not on One-Line | C1030 - Interiors - Doors - Automatic - Sliding | C1030 - Interiors - Doors | Automatic | Sliding | C. Interiors - Doors - Automatic - Sliding | C. Interiors - Doors | Automatic | Sliding | Automatic - Sliding | Each door assembly | Door Frame, 6" below upper hinge (or above UL label) | Automatic sliding doors use optical or motion detection sensors to activate their motorized opening and closing functions. These sensors are mounted over the automatic door or are integrated into the door framing from above or the side. |  | 21-03 10 30 25 | Interior Sliding Doors | 22-08 11 73 | Sliding Metal Fire doors | 23-17 11 13 19 | Sliding Metal Doors
Asset | C1030.25 | Not on One-Line | C1030 - Interiors - Doors - Automatic - Swing | C1030 - Interiors - Doors | Automatic | Swing | C. Interiors - Doors - Automatic - Swing | C. Interiors - Doors | Automatic | Swing | Automatic - Swing | Each door assembly | Door Frame, 6" below upper hinge (or above UL label) | Automatic swing doors use optical or motion detection sensors to activate their motorized opening and closing functions. These sensors are mounted over the automatic door or are integrated into the door framing from above or the side. |  | 21-03 10 30 10 | Interior Swinging Doors | 22-08 10 00 | Doors and Frames
Asset | C1030.70 | D10-2 | C1030 - Interiors - Doors - Linen Chute Discharge | C1030 - Interiors - Doors | Linen Chute Discharge |  | C. Interiors - Doors - Linen Chute Discharge | C. Interiors - Doors | Linen Chute Discharge |  | Linen Chute Discharge | Each discharge assembly, linked to chute | On discharge unit | This is the discharge portion of a linen chute which contains a fire-rated door which closes when a fusible link is compromised. The purpose of this door is to stop the spread of fire or smoke throughout the facility in case of a fire in the linen chute room. |  | 21-04 10 50 60 | Chutes | 22-14 91 33 | Laundry and Linen Chutes | 23-23 17 17 15 | Laundry and Linen Chutes
Asset | C1030.70 | D10-2 | C1030 - Interiors - Doors - Linen Chute Loading Hopper | C1030 - Interiors - Doors | Linen Chute Loading Hopper |  | C. Interiors - Doors - Linen Chute Loading Hopper | C. Interiors - Doors | Linen Chute Loading Hopper |  | Linen Chute Loading Hopper | Each door assembly, linked to chute | On outside of hopper by hinge | This is the loading portion of a linen chute which contains a self closing fire-rated door. The purpose of this door is to stop the spread of fire or smoke throughout the facility in case of a fire. |  | 21-04 10 50 60 | Chutes | 22-14 91 33 | Laundry and Linen Chutes | 23-23 17 17 15 | Laundry and Linen Chutes
Asset | C1030.70 | Not on One-Line | C1030 - Interiors - Doors - Rolling / Sliding Fire Door | C1030 - Interiors - Doors | Rolling / Sliding Fire Door |  | C. Interiors - Doors - Rolling / Sliding Fire Door | C. Interiors - Doors | Rolling / Sliding Fire Door |  | Rolling / Sliding Fire Door | Each door assembly | On Frame | This is a rated fire door that rolls and shuts an opening when a fusible link is compromised. |  | 21-03 10 30 25 | Interior Sliding Doors | 22-08 11 73 | Sliding Metal Fire doors | 23-17 11 31 11 13 | Fire Rated Rolling Doors
Asset | C1030.70 | Not on One-Line | C1030 - Interiors - Doors - Stairwell interrupter | C1030 - Interiors - Doors | Stairwell interrupter |  | C. Interiors - Doors - Stairwell interrupter | C. Interiors - Doors | Stairwell interrupter |  | Stairwell interrupter | Each assembly | On unit | A swinging gate that returns automatically to its closed position and utilized to direct movement when visibility is obscured. |  | 21-03 10 40 50 | Interior Gates | 22-08 34 00
Asset | C1030.70 | D10-2 | C1030 - Interiors - Doors - Trash Chute Discharge | C1030 - Interiors - Doors | Trash Chute Discharge |  | C. Interiors - Doors - Trash Chute Discharge | C. Interiors - Doors | Trash Chute Discharge |  | Trash Chute Discharge | Each discharge assembly, linked to chute | On discharge unit | This is the discharge portion of a trash chute which contains a fire-rated door which closes when a fusible link is compromised. The purpose of this door is to stop the spread of fire or smoke throughout the facility in case of a fire in the trash room. |  | 21-04 10 50 60 | Chutes | 22-14 91 82 | Trash Chutes | 23-39 45 25 17 13 | Refuse Chute Doors
Asset | C1030.70 | D10-2 | C1030 - Interiors - Doors - Trash Chute Loading Hopper | C1030 - Interiors - Doors | Trash Chute Loading Hopper |  | C. Interiors - Doors - Trash Chute Loading Hopper | C. Interiors - Doors | Trash Chute Loading Hopper |  | Trash Chute Loading Hopper | Each door assembly, linked to chute | On outside of hopper by hinge | This is the loading portion of a trash chute which contains a fire-rated hinged panel. The purpose of this door is to stop the spread of fire or smoke throughout a facility. |  | 21-04 10 50 60 | Chutes | 22-14 91 82 | Trash Chutes | 23-39 45 25 17 13 | Refuse Chute Doors
Asset | C1030.80 | Not on One-Line | C1030 - Interiors - Doors - Access Panel | C1030 - Interiors - Doors | Access Panel |  | C. Interiors - Doors - Access Panel | C. Interiors - Doors | Access Panel |  | Access Panel | Each access panel | On frame | Is a door or panel that can be removed to provide access to a shut-off valve, drain or other building element.
Asset | C1030.90 | Not on One-Line | C1030 - Interiors - Doors - Access Control Hardware | C1030 - Interiors - Doors | Access Control Hardware |  | C. Interiors - Doors - Access Control Hardware | C. Interiors - Doors | Access Control Hardware |  | Access Control Hardware | Each door assembly | Door Frame, 6" below upper hinge (or above UL label) | Any manual or electronic device such as key locks, cypher locks, electric strikes etc. mounted to the door or frame that restrict operation of the door. |  | 21-03 10 30 10 | Interior Swinging Doors | 22-08 10 00 | Doors and Frames
Asset | C1030.90 | Not on One-Line | C1030 - Interiors - Doors - Delayed Egress Hardware | C1030 - Interiors - Doors | Delayed Egress Hardware |  | C. Interiors - Doors - Delayed Egress Hardware | C. Interiors - Doors | Delayed Egress Hardware |  | Delayed Egress Hardware | Each door assembly | Door Frame, 6" below upper hinge (or above UL label) | Delayed egress hardware prevents a door from being opened from the egress side, usually for a period of 15 seconds. This type of device is often used to prevent theft, while maintaining life safety. |  | 21-03 10 30 10 | Interior Swinging Doors | 22-08 10 00 | Doors and Frames
Asset | C1030.90 | D70-1 | C1030 - Interiors - Doors - Maglock Door Release | C1030 - Interiors - Doors | Maglock Door Release |  | C. Interiors - Doors - Maglock Door Release | C. Interiors - Doors | Maglock Door Release |  | Maglock Door Release | Each unit | On unit | This is used to lock the door until access control releases it. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 16 | Fire Detection and Alarm Interfaces to Access Control Hardware | 23-17 19 11 31 15 | Electromagnetic Door Holders
Asset | C1030.90 | D70-1 | C1030 - Interiors - Doors - Magnetic Door Holder | C1030 - Interiors - Doors | Magnetic Door Holder |  | C. Interiors - Doors - Magnetic Door Holder | C. Interiors - Doors | Magnetic Door Holder |  | Magnetic Door Holder | Each unit | On unit mounted to wall (the magnet) | This is used to hold the door open, tied to the fire alarm system to release the door in certain scenarios. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 16 | Fire Detection and Alarm Interfaces to Access Control Hardware | 23-17 19 11 31 15 | Electromagnetic Door Holders
Supplemental Elements | C1030.90.99 | n/a | C1030 - Interiors - Doors - [Supplemental Elements] Doors | C1030 - Interiors - Doors | [Supplemental Elements] Doors |  | C. Interiors - Doors - [Supplemental Elements] Doors | C. Interiors - Doors | [Supplemental Elements] Doors |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D1010 |  | D1010 - Conveying - Vertical Transportation | D1010 - Conveying - Vertical Transportation |  |  | D. Vertical Transportation | D. Vertical Transportation | [5 empty] | General Category |  | 21-04 10 10 | Vertical Conveying Systems | 22-14 00 00 | Conveying Equipment | 23-23 11 00 | Vertical Transportation Equipment
System | D1010 | Not on One-Line | D1010 - Conveying - Vertical Transportation - (System) Elevators | D1010 - Conveying - Vertical Transportation | (System) Elevators |  | D. Vertical Transportation - (System) Elevators | D. Vertical Transportation | (System) Elevators |  | SYS Elevators ([Elevator Bank]) | Each building, possibly segmented horizontally by floor. | Track by Elevator Number or AHJ ID | Generic representation of all elevators.
Asset | D1010.10 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Freight Elevator | D1010 - Conveying - Vertical Transportation | Freight Elevator |  | D. Vertical Transportation - Freight Elevator | D. Vertical Transportation | Freight Elevator |  | Freight Elevator | Each elevator | Track by Elevator Number or AHJ ID | An elevator designed to carry materials and people responsible for the construction, maintenance and operations of a facility. |  | 21-04 10 10 10 | Elevators | 22-14 21 13 | Electric Traction Freight Elevators | 23-23 11 11 13 11 | Freight Hydraulic Elevators
Asset | D1010.10 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Passenger / Service Elevator | D1010 - Conveying - Vertical Transportation | Passenger / Service Elevator |  | D. Vertical Transportation - Passenger / Service Elevator | D. Vertical Transportation | Passenger / Service Elevator |  | Passenger / Service Elevator | Each elevator | Track by Elevator Number or AHJ ID | An elevator of any type that is integral to the building. |  | 21-04 10 10 10 | Elevators | 22-14 24 00 | Hydraulic Elevators | 23-23 11 11 13 13 | Passenger Hydraulic Elevators
Asset | D1010.10 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Passenger Elevator | D1010 - Conveying - Vertical Transportation | Passenger Elevator |  | D. Vertical Transportation - Passenger Elevator | D. Vertical Transportation | Passenger Elevator |  | Passenger Elevator | Each elevator | Track by Elevator Number or AHJ ID | An elevator designed to carry people who either visit or work in the facility. |  | 21-04 10 10 10 | Elevators | 22-14 24 23 | Hydraulic Passenger Elevators | 23-23 11 11 13 13 | Passenger Hydraulic Elevators
Asset | D1010.10 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Patient Elevator | D1010 - Conveying - Vertical Transportation | Patient Elevator |  | D. Vertical Transportation - Patient Elevator | D. Vertical Transportation | Patient Elevator |  | Patient Elevator | Each elevator | Track by Elevator Number or AHJ ID | A n elevator designed to carry patients only, along with their caregivers.. |  | 21-04 10 10 10 | Elevators | 22-14 20 00 | Elevators | 23-23 11 11 13 13 | Passenger Hydraulic Elevators
Asset | D1010.10 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Service Elevator | D1010 - Conveying - Vertical Transportation | Service Elevator |  | D. Vertical Transportation - Service Elevator | D. Vertical Transportation | Service Elevator |  | Service Elevator | Each elevator | Track by Elevator Number or AHJ ID | A vertical transportation device used by facility personnel to deliver material and maintenance items. This elevator is normally not allowed for public use. |  | 21-04 10 10 10 | Elevators | 22-14 24 43 | Hydraulic Service Elevators | 23-23 11 11 13 17 | Service Hydraulic Elevators
Asset | D1010.20 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Material Lift | D1010 - Conveying - Vertical Transportation | Material Lift |  | D. Vertical Transportation - Material Lift | D. Vertical Transportation | Material Lift |  | Material Lift | Each lift | On control panel | A vertical transportation device not designed for passengers. Typically elevates less than one story. Permanently installed. |  | 21-04 10 10 20 | Lifts | 22-14 40 00 | Lifts | 23-23 13 11 | Lifts
Asset | D1010.20 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Wheelchair Lift | D1010 - Conveying - Vertical Transportation | Wheelchair Lift |  | D. Vertical Transportation - Wheelchair Lift | D. Vertical Transportation | Wheelchair Lift |  | Wheelchair Lift | Each lift | On control panel | A fixed vertical transportation device of a size and capacity specifically to raise wheelchairs short distances. |  | 21-04 10 10 20 | Lifts | 22-14 42 00 | Wheelchair Lifts | 23-23 13 11 25 | Wheel Chair Lifts
Asset | D1010.30 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Escalators | D1010 - Conveying - Vertical Transportation | Escalators |  | D. Vertical Transportation - Escalators | D. Vertical Transportation | Escalators |  | Escalators | Each escalator | Track by Elevator Number or AHJ ID | A moving staircase consisting of an endlessly circulating belt of steps driven by a motor, conveying people between different levels of an asset. |  | 21-04 10 10 30 | Escalators | 22-14 31 00 | Escalators | 23-23 11 13 | Escalators
Asset | D1010.50 | Not on One-Line | D1010 - Conveying - Vertical Transportation - Dumbwaiter | D1010 - Conveying - Vertical Transportation | Dumbwaiter |  | D. Vertical Transportation - Dumbwaiter | D. Vertical Transportation | Dumbwaiter |  | Dumbwaiter | Each dumbwaiter | Track by Elevator Number or AHJ ID | A small elevator for carrying things, especially food and dishes, between the floors of a building. |  | 21-04 10 10 50 | Dumbwaiters | 22-14 10 00 | Dumbwaiters | 23-23 17 11 | Dumbwaiters
Supplemental Elements | D1010.99 | n/a | D1010 - Conveying - Vertical Transportation - [Supplemental Elements] Vertical Transportation | D1010 - Conveying - Vertical Transportation | [Supplemental Elements] Vertical Transportation |  | D. Vertical Transportation - [Supplemental Elements] Vertical Transportation | D. Vertical Transportation | [Supplemental Elements] Vertical Transportation |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D1050 |  | D1050 - Conveying - Material Handling | D1050 - Conveying - Material Handling |  |  | D. Material Handling | D. Material Handling | [5 empty] | General Category |  | 21-04 10 50 | Material Handling |  |  | 23-23 17 00 | Materials Handling
System | D1050.40 | Not on One-Line | D1050 - Conveying - Material Handling - (System) Conveyor | D1050 - Conveying - Material Handling | (System) Conveyor |  | D. Material Handling - (System) Conveyor | D. Material Handling | (System) Conveyor |  | SYS Conveyor ([Area Served]) | Each conveyor | No barcode - Track by location | Material conveying equipment. |  | 21-04 10 50 40 | Conveyors | 22-41 12 13 | Bulk Material Conveyors | 23-23 17 15 | Conveyors
System | D1050.60 | D10-2 | D1050 - Conveying - Material Handling - (System) Linen Chute | D1050 - Conveying - Material Handling | (System) Linen Chute |  | D. Material Handling - (System) Linen Chute | D. Material Handling | (System) Linen Chute |  | SYS Linen Chute ([Area Served]) | Each Chute | On casing at discharge point | A metal casing built into the building structure and fitted with access hatches at each floor level to allow soiled linen to be carried by gravity to collection at the lowest point.
System | D1050.60 | D10-2 | D1050 - Conveying - Material Handling - (System) Trash Chute | D1050 - Conveying - Material Handling | (System) Trash Chute |  | D. Material Handling - (System) Trash Chute | D. Material Handling | (System) Trash Chute |  | SYS Trash Chute ([Area Served]) | Each Chute | On casing at discharge point | A metal casing built into the building structure and fitted with access hatches at each floor level to allow refuse to be carried by gravity to collection at the lowest point.
System | D1050.70 | D10-1 | D1050 - Conveying - Material Handling - (System) Pneumatic Tube | D1050 - Conveying - Material Handling | (System) Pneumatic Tube |  | D. Material Handling - (System) Pneumatic Tube | D. Material Handling | (System) Pneumatic Tube |  | SYS Pneumatic Tube ([Area Served]) | Each system | No barcode - Track by system | Piece of conveying equipment used for multiple things including specimens and medications. |  | 21-04 10 50 70 | Pneumatic Tube Systems | 22-14 92 00 | Pneumatic Tube Systems | 23-23 17 21 | Pneumatic Tube Systems
Asset | D1050.70 | D10-1 | D1050 - Conveying - Material Handling - Pneumatic Tube System - Blower | D1050 - Conveying - Material Handling | Pneumatic Tube System - Blower |  | D. Material Handling - Pneumatic Tube System - Blower | D. Material Handling | Pneumatic Tube System - Blower |  | PTS - Blower | Each unit | On casing | An exhauster that creates a vacuum in the tube system providing the motive power to move the carriers. |  | 21-04 10 50 70 | Pneumatic Tube Systems | 22-14 92 00 | Pneumatic Tube Systems | 23-23 17 21 15 | Pneumatic Tube Vacuum Boxes
Asset | D1050.70 | D10-1 | D1050 - Conveying - Material Handling - Pneumatic Tube System - Station | D1050 - Conveying - Material Handling | Pneumatic Tube System - Station |  | D. Material Handling - Pneumatic Tube System - Station | D. Material Handling | Pneumatic Tube System - Station |  | PTS - Station | Each unit | On casing | Operator interface point to allow carriers to be entered and removed from the system. |  | 21-04 10 50 70 | Pneumatic Tube Systems | 22-14 92 00 | Pneumatic Tube Systems | 23-23 17 21 11 | Pneumatic Tubes
Asset | D1050.70 | D10-1 | D1050 - Conveying - Material Handling - Pneumatic Tube System - Transfer Station | D1050 - Conveying - Material Handling | Pneumatic Tube System - Transfer Station |  | D. Material Handling - Pneumatic Tube System - Transfer Station | D. Material Handling | Pneumatic Tube System - Transfer Station |  | PTS - Transfer Station | Each unit | On casing | An automated diverting station that aligns tubes for routing carriers to specified locations. |  | 21-04 10 50 70 | Pneumatic Tube Systems | 22-14 92 00 | Pneumatic Tube Systems | 23-23 17 21 13 | Pneumatic Tube Controls
Supplemental Elements | D1050.99 | n/a | D1050 - Conveying - Material Handling - [Supplemental Elements] Material Handling | D1050 - Conveying - Material Handling | [Supplemental Elements] Material Handling |  | D. Material Handling - [Supplemental Elements] Material Handling | D. Material Handling | [Supplemental Elements] Material Handling |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D1080 |  | D1080 - Conveying - Operable Access Systems | D1080 - Conveying - Operable Access Systems |  |  | D. Operable Access Systems | D. Operable Access Systems | [5 empty] | General Category |  | 21-04 10 80 | Operable Access Systems | 22-14 80 00 | Scaffolding | 23-23 25 00 | Scaffolding
System | D1080.50 | Not on One-Line | D1080 - Conveying - Operable Access Systems - (System) Window Cleaning | D1080 - Conveying - Operable Access Systems | (System) Window Cleaning |  | D. Operable Access Systems - (System) Window Cleaning | D. Operable Access Systems | (System) Window Cleaning |  | SYS Window Cleaning | Each Access System | On control panel | Typically a roof mounted gantry permanently installed that supports a scaffold lowered along the building exterior normally for cleaning the façade. |  | 21-04 10 80 50 | Building Envelope Access | 22-14 84 13 | Window Washing Scaffolding | 23-27 71 11 | Window Washing Systems
Supplemental Elements | D1080.99 | n/a | D1080 - Conveying - Operable Access Systems - [Supplemental Elements] Operable Access Systems | D1080 - Conveying - Operable Access Systems | [Supplemental Elements] Operable Access Systems |  | D. Operable Access Systems - [Supplemental Elements] Operable Access Systems | D. Operable Access Systems | [Supplemental Elements] Operable Access Systems |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2010 |  | D2010 - Plumbing - Domestic Water | D2010 - Plumbing - Domestic Water |  |  | D. Plumbing - Domestic Water | D. Plumbing - Domestic Water | [5 empty] | General Category |  | 21-04 20 10 | Domestic Water Distribution | 22-22 11 00 | Facility Water Distribution
System | D2010 | Not on One-Line | D2010 - Plumbing - Domestic Water - (System) Domestic Hot Water | D2010 - Plumbing - Domestic Water | (System) Domestic Hot Water |  | D. Plumbing - Domestic Water - (System) Domestic Hot Water | D. Plumbing - Domestic Water | (System) Domestic Hot Water |  | SYS Domestic Hot ([Area Served]) | Each loop | No barcode - Track by location | Generic representation of all branches with domestic hot water loops.
System | D2010 | Not on One-Line | D2010 - Plumbing - Domestic Water - (System) Domestic Water | D2010 - Plumbing - Domestic Water | (System) Domestic Water |  | D. Plumbing - Domestic Water - (System) Domestic Water | D. Plumbing - Domestic Water | (System) Domestic Water |  | SYS Domestic Cold ([Area Served]) | Each system or system branch | No barcode - Track by location | Generic representation of all cold domestic water system.
System | D2010 | Not on One-Line | D2010 - Plumbing - Domestic Water - (System) Water Treatment and Filtration | D2010 - Plumbing - Domestic Water | (System) Water Treatment and Filtration |  | D. Plumbing - Domestic Water - (System) Water Treatment and Filtration | D. Plumbing - Domestic Water | (System) Water Treatment and Filtration |  | SYS Water Treatment/Filtration ([Area Served]) | Each system | On control panel | System that typically involves injection of bulk chemicals into a raw water process in order to bring it to some required quality specification and/or mechanical filtration. |  | 21-04 20 10 90 | Domestic Water Distribution Supplementary Components | 22-43 32 69 | Chemical Feed Systems | 23-27 55 31 11 | Liquid Chemical Feeders
Asset | D2010.10 | Not on One-Line | D2010 - Plumbing - Domestic Water - Break Tank | D2010 - Plumbing - Domestic Water | Break Tank |  | D. Plumbing - Domestic Water - Break Tank | D. Plumbing - Domestic Water | Break Tank |  | Break Tank | Each tank | On control panel | A non-pressurized, closed water tank, with an air gap to ensure zero backflow. It interrupts or 'breaks' the connection to the water source. |  | 21-04 20 10 10 | Facility Potable-Water Storage Tanks | 22-22 12 00 | Facility Potable-Water Storage Tanks | 23-27 29 15 | Specialized Tanks
Asset | D2010.10 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Storage Tank | D2010 - Plumbing - Domestic Water | Domestic Hot Water Storage Tank |  | D. Plumbing - Domestic Water - Domestic Hot Water Storage Tank | D. Plumbing - Domestic Water | Domestic Hot Water Storage Tank |  | Domestic Hot Water Storage Tank | Each tank to be barcoded | On control panel | A device who's stole purpose is to store domestic hot water between 105F and 140F. Water is produced by a separate heat exchanger or other means. Tank normally sized to address demand use. An inventory of these devices can support ASHRAE 188. |  | 21-04 20 10 10 | Facility Potable-Water Storage Tanks | 22-22 12 00 |  | 23-31 29 13 | Hot Water Tank Heaters
Asset | D2010.10 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Water Pump | D2010 - Plumbing - Domestic Water | Domestic Water Pump |  | D. Plumbing - Domestic Water - Domestic Water Pump | D. Plumbing - Domestic Water | Domestic Water Pump |  | Domestic Water Pump | Each pump set (not each pump) | On control panel | This is a pump that takes city water and pumps it up to a house tank. Normally used in building more they 5 stories high as city water pressure cannot provide adequate pressure to get the water to the upper floors. |  | 21-04 20 10 | Domestic Water Distribution | 22-22 11 00 |  | 23-27 17 00 | Pumps
Asset | D2010.10 | D20-1 | D2010 - Plumbing - Domestic Water - House Tank | D2010 - Plumbing - Domestic Water | House Tank |  | D. Plumbing - Domestic Water - House Tank | D. Plumbing - Domestic Water | House Tank |  | House Tank | Each unit | On control panel, if no control panel on dunnage under tank | A tank used to maintain pressure in the domestic water and/or fire protection systems and is generally installed at the top of a high rise building. Tank is serviced by a house pump that boosts the city water pressure so it can reach high enough to fill the house tank. |  | 21-04 20 10 10 | Facility Potable-Water Storage Tanks | 22-22 12 00 |  | 23-27 29 00 | Tanks and Storage Structures
Asset | D2010.10 | Not on One-Line | D2010 - Plumbing - Domestic Water - Potable Water Storage Tank | D2010 - Plumbing - Domestic Water | Potable Water Storage Tank |  | D. Plumbing - Domestic Water - Potable Water Storage Tank | D. Plumbing - Domestic Water | Potable Water Storage Tank |  | Potable Water Storage Tank | Each unit | On control panel | Domestic Water Storage tank, typically at an upper floor level. |  | 21-04 20 10 10 | Facility Potable-Water Storage Tanks | 22-22 12 00 |  | 23-27 29 15 | Specialized Tanks
Asset | D2010.10 | D20-1 | D2010 - Plumbing - Domestic Water - Surge Tank | D2010 - Plumbing - Domestic Water | Surge Tank |  | D. Plumbing - Domestic Water - Surge Tank | D. Plumbing - Domestic Water | Surge Tank |  | Surge Tank | Each tank | On control panel | Tank intended to neutralize sudden changes of pressure in the flow by filling when the pressure increases and emptying when it drops. |  | 21-04 20 10 10 | Facility Potable-Water Storage Tanks | 22-22 12 00 |  | 23-27 29 15 | Specialized Tanks
Asset | D2010.20 | Not on One-Line | D2010 - Plumbing - Domestic Water - Dialysis Hookup | D2010 - Plumbing - Domestic Water | Dialysis Hookup |  | D. Plumbing - Domestic Water - Dialysis Hookup | D. Plumbing - Domestic Water | Dialysis Hookup |  | Dialysis Hookup | Each unit | On inlet side of pipe directly or with chain and tag before the assembly. | A connection the domestic system that provides water at a specific temperature and usually at a specified pressure. |  | 21-04 20 10 90 | Domestic Water Distribution Supplementary Components | 22-22 43 00 | Dialysis Boxes | 23-25 23 13 11 13 | Dialysis Boxes
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Boiler | D2010 - Plumbing - Domestic Water | Domestic Hot Water Boiler |  | D. Plumbing - Domestic Water - Domestic Hot Water Boiler | D. Plumbing - Domestic Water | Domestic Hot Water Boiler |  | Domestic Hot Water Boiler | Each unit | On control panel, if no control panel on clean space next to boiler "name" | A device that indirectly produces domestic hot water |  | 21-04 20 10 20 | Domestic Water Equipment | 22-23 52 13 | Electric Boilers | 23-33 11 22 | Electric Boilers
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Boiler - Electric | D2010 - Plumbing - Domestic Water | Domestic Hot Water Boiler | Electric | D. Plumbing - Domestic Water - Domestic Hot Water Boiler - Electric | D. Plumbing - Domestic Water | Domestic Hot Water Boiler | Electric | Domestic Hot Water Boiler - Electric | Each unit | On control panel, if no control panel on clean space next to boiler "name" | A device that indirectly produces domestic hot water by using electrical energy. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-23 52 13 | Electric Boilers | 23-33 11 22 | Electric Boilers
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Boiler - Gas | D2010 - Plumbing - Domestic Water | Domestic Hot Water Boiler | Gas | D. Plumbing - Domestic Water - Domestic Hot Water Boiler - Gas | D. Plumbing - Domestic Water | Domestic Hot Water Boiler | Gas | Domestic Hot Water Boiler - Gas | Each unit | On control panel, if no control panel on clean space next to boiler "name" | A device that indirectly produces domestic hot water by using natural gas or propane. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-23 52 00 | Heating Boilers | 23-33 11 15 | Fire Tube Boilers
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Boiler - Oil | D2010 - Plumbing - Domestic Water | Domestic Hot Water Boiler | Oil | D. Plumbing - Domestic Water - Domestic Hot Water Boiler - Oil | D. Plumbing - Domestic Water | Domestic Hot Water Boiler | Oil | Domestic Hot Water Boiler - Oil | Each unit | On control panel, if no control panel on clean space next to boiler "name" | A device that indirectly produces domestic hot water by using oil. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-23 52 00 | Heating Boilers | 23-33 11 19 | Sectionalized Cast Iron Boilers
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Circulating Pump | D2010 - Plumbing - Domestic Water | Domestic Hot Water Circulating Pump |  | D. Plumbing - Domestic Water - Domestic Hot Water Circulating Pump | D. Plumbing - Domestic Water | Domestic Hot Water Circulating Pump |  | Domestic Hot Water Circulating Pump | Pump at heater should be its own asset, unless it is tracked as a sub-asset to the heater. (Small circulating pumps are No barcode and run to failure.) | On control panel | A pump that circulates domestic hot water from the furthest point of distribution to the source in order to maintain the proper discharge temperature and prevent the spread of legionella. |  | 21-04 20 10 | Domestic Water Distribution | 22-22 11 23 | Domestic Water Pumps | 23-31 29 00 | Hot Water Heaters
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Heater | D2010 - Plumbing - Domestic Water | Domestic Hot Water Heater |  | D. Plumbing - Domestic Water - Domestic Hot Water Heater | D. Plumbing - Domestic Water | Domestic Hot Water Heater |  | Domestic Hot Water Heater | Each Water Heater. The Pump could a sub-asset, or it could be its own, separate asset | On control panel | A device that produces domestic hot water (normally between 115F and 140F). Unit can produce the water instantaneously or is provided with a tank to store the water to address demand use. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-22 33 13 | Instantaneous Electric Domestic Water Heaters | 23-31 29 11 11 | Electric Instantaneous Hot Water Heaters
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Heater - Electric | D2010 - Plumbing - Domestic Water | Domestic Hot Water Heater | Electric | D. Plumbing - Domestic Water - Domestic Hot Water Heater - Electric | D. Plumbing - Domestic Water | Domestic Hot Water Heater | Electric | Domestic Hot Water Heater - Electric | Each Water Heater. The Pump could a sub-asset, or it could be its own, separate asset | On control panel | A device that produces domestic hot water (normally between 115F and 140F) using electrical energy. Unit can produce the water instantaneously or is provided with a tank to store the water to address demand use. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-22 33 13 | Instantaneous Electric Domestic Water Heaters | 23-31 29 11 11 | Electric Instantaneous Hot Water Heaters
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Heater - Gas | D2010 - Plumbing - Domestic Water | Domestic Hot Water Heater | Gas | D. Plumbing - Domestic Water - Domestic Hot Water Heater - Gas | D. Plumbing - Domestic Water | Domestic Hot Water Heater | Gas | Domestic Hot Water Heater - Gas | Each Water Heater. The Pump could a sub-asset, or it could be its own, separate asset | On control panel | A device that produces domestic hot water (normally between 115F and 140F) using natural; gas or propane. Unit can produce the water instantaneously or is provided with a tank to store the water to address demand use. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-22 34 00 | Fuel-Fired Domestic Water Heaters | 23-31 29 11 13 | Gas Instantaneous Hot Water Heaters
Asset | D2010.20 | Not on One-Line | D2010 - Plumbing - Domestic Water - Domestic Hot Water Heater - Steam (High Pressure) | D2010 - Plumbing - Domestic Water | Domestic Hot Water Heater | Steam (High Pressure) | D. Plumbing - Domestic Water - Domestic Hot Water Heater - Steam (High Pressure) | D. Plumbing - Domestic Water | Domestic Hot Water Heater | Steam (High Pressure) | Domestic Hot Water Heater - Steam (High Pressure) | Each Water Heater. The Pump could a sub-asset, or it could be its own, separate asset | On control panel | A device that produces domestic hot water (normally between 115F and 140F) using high pressure steam. Unit can be produce the water instantaneously or is provided with a tank to store the water to address demand use. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-22 35 23 | Circulating, Domestic Water Heat Exchangers | 23-31 29 11 | Instantaneous Hot Water Heaters
Asset | D2010.20 | Not on One-Line | D2010 - Plumbing - Domestic Water - Domestic Hot Water Heater - Steam (Low Pressure) | D2010 - Plumbing - Domestic Water | Domestic Hot Water Heater | Steam (Low Pressure) | D. Plumbing - Domestic Water - Domestic Hot Water Heater - Steam (Low Pressure) | D. Plumbing - Domestic Water | Domestic Hot Water Heater | Steam (Low Pressure) | Domestic Hot Water Heater - Steam (Low Pressure) | Each Water Heater. The Pump could a sub-asset, or it could be its own, separate asset | On control panel | A device that produces domestic hot water (normally between 115F and 140F) using low pressure steam. Unit can be produce the water instantaneously or is provided with a tank to store the water to address demand use. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-22 35 23 | Circulating, Domestic Water Heat Exchangers | 23-31 29 13 15 | Hot Water Tank Steam Heaters
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Hot Water Treatment Unit | D2010 - Plumbing - Domestic Water | Domestic Hot Water Treatment Unit |  | D. Plumbing - Domestic Water - Domestic Hot Water Treatment Unit | D. Plumbing - Domestic Water | Domestic Hot Water Treatment Unit |  | Domestic Hot Water Treatment Unit | Each unit | On control panel | Covers multiple water treatment technologies for purifying domestic water (e.g.: Copper Silver) |  | 21-04 20 10 90 | Domestic Water Distribution Supplementary Components | 22-46 07 53 | Packaged Wastewater Treatment Equipment
Asset | D2010.20 | D20-1 | D2010 - Plumbing - Domestic Water - Domestic Water Booster Pump | D2010 - Plumbing - Domestic Water | Domestic Water Booster Pump |  | D. Plumbing - Domestic Water - Domestic Water Booster Pump | D. Plumbing - Domestic Water | Domestic Water Booster Pump |  | Domestic Water Booster Pump | Each pump set (not each pump) | On control panel | This a pumping system that operates with a variable frequency drive or relief valve that is used in lieu of a house tank to maintain building pressure. |  | 21-04 20 10 | Domestic Water Distribution | 22-22 11 00 |  | 23-27 17 00 | Pumps
Asset | D2010.20 | Not on One-Line | D2010 - Plumbing - Domestic Water - Exterior Hose Bib | D2010 - Plumbing - Domestic Water | Exterior Hose Bib |  | D. Plumbing - Domestic Water - Exterior Hose Bib | D. Plumbing - Domestic Water | Exterior Hose Bib |  | Exterior Hose Bib | Each location | Hang as a tag inside valve box if equipped or off neck of valve | A type of water supply valve with a threaded male connection for connecting washing machine and general utility hoses such as garden hoses. |  | 21-04 20 10 60 | Plumbing Fixtures | 22-22 40 00
Asset | D2010.20 | HD-2 | D2010 - Plumbing - Domestic Water - Sand Filter | D2010 - Plumbing - Domestic Water | Sand Filter |  | D. Plumbing - Domestic Water - Sand Filter | D. Plumbing - Domestic Water | Sand Filter |  | Sand Filter | Each unit | On unit (other than replicable parts) | A filtration unit designed to remove larger particles from the water supply. Unit is periodically backwashed to regenerate the unit. |  | 21-04 20 10 90 | Domestic Water Distribution Supplementary Components | 22-22 32 26 | Domestic-Water Sand Filters | 23-27 55 11 11 | Water Filters
Asset | D2010.20 | Not on One-Line | D2010 - Plumbing - Domestic Water - UV Filter | D2010 - Plumbing - Domestic Water | UV Filter |  | D. Plumbing - Domestic Water - UV Filter | D. Plumbing - Domestic Water | UV Filter |  | UV Filter | Each filter; pump may be sub-asset | On unit (other than replaceable parts) | A chamber equipped with an ultraviolet source utilized to kill waterborne biological growth as water passes through the device. |  | 21-04 20 10 90 | Domestic Water Distribution Supplementary Components | 22-22 32 00 | Domestic Water Filtration Equipment | 23-27 55 25 | Liquid Disinfecting Ultraviolet Lighting
Asset | D2010.20 | Not on One-Line | D2010 - Plumbing - Domestic Water - Water Softener | D2010 - Plumbing - Domestic Water | Water Softener |  | D. Plumbing - Domestic Water - Water Softener | D. Plumbing - Domestic Water | Water Softener |  | Water Softener | Each softener | On control panel | Treatment system that uses ion exchange to remove hardness and scale from raw water. Sizes range from those intended for residential use up to large industrial boilers. |  | 21-04 20 10 90 | Domestic Water Distribution Supplementary Components | 22-22 31 00 | Domestic Water Softeners | 23-27 55 27 11 | Water Softeners
Asset | D2010.20 | Not on One-Line | D2010 - Plumbing - Domestic Water - Water Submeter | D2010 - Plumbing - Domestic Water | Water Submeter |  | D. Plumbing - Domestic Water - Water Submeter | D. Plumbing - Domestic Water | Water Submeter |  | Water Submeter | Each submeter | On unit | A standard water meter but utilized for measuring only a portion of the water system, typically to a tenant or a specific water using process. |  | 21-04 20 10 90 | Domestic Water Distribution Supplementary Components | 22-22 05 19
Asset | D2010.40 | D20-1 | D2010 - Plumbing - Domestic Water - Backflow Preventer - Domestic Water | D2010 - Plumbing - Domestic Water | Backflow Preventer - Domestic Water |  | D. Plumbing - Domestic Water - Backflow Preventer - Domestic Water | D. Plumbing - Domestic Water | Backflow Preventer - Domestic Water |  | Backflow Preventer - Domestic Water | Each backflow preventer | On tag, chained to preventer | This device is required wherever potable water systems are piped into non-potable systems. These plumbing fixtures sense conditions wherein the non-potable system pressure exceeds the potable system, raising the potential for contamination, and triggering a disconnection of the two systems, along with a dumping of flow. |  | 21-04 20 10 20 | Domestic Water Equipment | 22-33 12 13 13 | Water Supply Backflow Preventer Assemblies | 23-27 31 11 | Backflow Preventors
Asset | D2010.40 | D20-1 | D2010 - Plumbing - Domestic Water - Mixing / Recirculation Valve | D2010 - Plumbing - Domestic Water | Mixing / Recirculation Valve |  | D. Plumbing - Domestic Water - Mixing / Recirculation Valve | D. Plumbing - Domestic Water | Mixing / Recirculation Valve |  | Mixing / Recirculation Valve | Each valve | On valve body | This is a valve that regulates the temperature of domestic hot water by mixing domestic cold water with domestic hot water. Can be installed at point of use or as part of an overall system design. |  | 21-04 20 10 60 | Plumbing Fixtures | 22-22 40 00 |  | 23-27 31 29 | Mixing Valves
Asset | D2010.60 | Not on One-Line | D2010 - Plumbing - Domestic Water - Commercial Garbage Disposal | D2010 - Plumbing - Domestic Water | Commercial Garbage Disposal |  | D. Plumbing - Domestic Water - Commercial Garbage Disposal | D. Plumbing - Domestic Water | Commercial Garbage Disposal |  | Commercial Garbage Disposal | Each unit | On casing | A heavy duty device designed to reduce kitchen waste to a consistency suitable for passage into the sanitary system.
Asset | D2010.60 | Not on One-Line | D2010 - Plumbing - Domestic Water - Drinking Fountains and Cooler | D2010 - Plumbing - Domestic Water | Drinking Fountains and Cooler |  | D. Plumbing - Domestic Water - Drinking Fountains and Cooler | D. Plumbing - Domestic Water | Drinking Fountains and Cooler |  | Drinking Fountains and Cooler | Each fountain and cooler | On casing | A wall or floor mounted unit that is provided with a refrigeration unit, filters and controls to provide cool drinking water to users. |  | 21-04 20 10 60 | Plumbing Fixtures | 22-22 47 00 | Drinking Fountains and Water Coolers | 23-31 31 11 | Drinking Fountain With Coolers
Asset | D2010.60 | Not on One-Line | D2010 - Plumbing - Domestic Water - Emergency Eye Wash and Shower Combination | D2010 - Plumbing - Domestic Water | Emergency Eye Wash and Shower Combination |  | D. Plumbing - Domestic Water - Emergency Eye Wash and Shower Combination | D. Plumbing - Domestic Water | Emergency Eye Wash and Shower Combination |  | Emergency Eye Wash and Shower Combination | Each unit | Hang as a tag visibly off unit | This is a combination unit. The emergency eye wash portion is used to drench or flush the eyes with water when dust, irritants, or chemicals enter the eye. The emergency shower portion is provided in areas of chemical use to allow users to cascades water over the whole body to cleanse themselves in case of an accident. |  | 21-04 20 10 60 | Plumbing Fixtures | 22-22 45 33 | Combination Emergency Fixture Units | 23-29 37 15 11 | Combination Emergency Showers
Asset | D2010.60 | Not on One-Line | D2010 - Plumbing - Domestic Water - Emergency Eye Wash Station | D2010 - Plumbing - Domestic Water | Emergency Eye Wash Station |  | D. Plumbing - Domestic Water - Emergency Eye Wash Station | D. Plumbing - Domestic Water | Emergency Eye Wash Station |  | Emergency Eye Wash Station | Each unit | Hang as a tag visibly off unit | Emergency eye wash equipment is used to drench or flush the eyes with water when dust, irritants, or chemicals enter the eye. |  | 21-04 20 10 60 | Plumbing Fixtures | 22-22 45 16 | Eyewash Equipment | 23-29 37 13 | Emergency Eye Wash Stations
Asset | D2010.60 | Not on One-Line | D2010 - Plumbing - Domestic Water - Emergency Shower | D2010 - Plumbing - Domestic Water | Emergency Shower |  | D. Plumbing - Domestic Water - Emergency Shower | D. Plumbing - Domestic Water | Emergency Shower |  | Emergency Shower | Each unit | Hang as a tag visibly off unit | This is a unit that is provided in areas of chemical use to allow users to cascade water over the whole body to cleanse themselves in case of an accident. |  | 21-04 20 10 60 | Plumbing Fixtures | 22-22 45 13 | Emergency Showers | 23-29 37 15 | Emergency Showers
Asset | D2010.60 | Not on One-Line | D2010 - Plumbing - Domestic Water - Plumbing Fixtures | D2010 - Plumbing - Domestic Water | Plumbing Fixtures |  | D. Plumbing - Domestic Water - Plumbing Fixtures | D. Plumbing - Domestic Water | Plumbing Fixtures |  | Plumbing Fixtures | Each unit | On unit if needed | Any of a group of end use devices such as sinks, hand wash stations, slop sinks, etc. Classification often used for water testing or general inspection. |  | 21-04 20 10 90 | Domestic Water Distribution Supplementary Components | 22-22 05 19
Asset | D2010.60 | Not on One-Line | D2010 - Plumbing - Domestic Water - Scrub Sink | D2010 - Plumbing - Domestic Water | Scrub Sink |  | D. Plumbing - Domestic Water - Scrub Sink | D. Plumbing - Domestic Water | Scrub Sink |  | Scrub Sink | Each scrub sink | In a visible location that won't get wet | Also referred to as surgical sinks or medical sinks, are used in Operating Rooms. They serve as the scrub station for surgeons and other OR staff to scrub their hands and arms before an invasive procedure. |  | 21-04 20 10 60 | Plumbing Fixtures | 23-25 47 11 15 13 | Clinic Scrub Sinks | 23-25 47 11 15 13 | Clinic Scrub Sinks
Supplemental Elements | D2010.99 | n/a | D2010 - Plumbing - Domestic Water - [Supplemental Elements] Domestic Hot Water | D2010 - Plumbing - Domestic Water | [Supplemental Elements] Domestic Hot Water |  | D. Plumbing - Domestic Water - [Supplemental Elements] Domestic Hot Water | D. Plumbing - Domestic Water | [Supplemental Elements] Domestic Hot Water |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Supplemental Elements | D2010.99 | n/a | D2010 - Plumbing - Domestic Water - [Supplemental Elements] Domestic Water | D2010 - Plumbing - Domestic Water | [Supplemental Elements] Domestic Water |  | D. Plumbing - Domestic Water - [Supplemental Elements] Domestic Water | D. Plumbing - Domestic Water | [Supplemental Elements] Domestic Water |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Supplemental Elements | D2010.99 | n/a | D2010 - Plumbing - Domestic Water - [Supplemental Elements] Water Treatment and Filtration | D2010 - Plumbing - Domestic Water | [Supplemental Elements] Water Treatment and Filtration |  | D. Plumbing - Domestic Water - [Supplemental Elements] Water Treatment and Filtration | D. Plumbing - Domestic Water | [Supplemental Elements] Water Treatment and Filtration |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2020 |  | D2020 - Plumbing - Sanitary Drainage | D2020 - Plumbing - Sanitary Drainage |  |  | D. Plumbing - Sanitary Drainage | D. Plumbing - Sanitary Drainage | [5 empty] | General Category |  | 21-04 20 20 | Sanitary Drainage | 22-22 13 00
System | D2020 | Not on One-Line | D2020 - Plumbing - Sanitary Drainage - (System) Sanitary Drainage | D2020 - Plumbing - Sanitary Drainage | (System) Sanitary Drainage |  | D. Plumbing - Sanitary Drainage - (System) Sanitary Drainage | D. Plumbing - Sanitary Drainage | (System) Sanitary Drainage |  | SYS Sanitary Drainage ([Area Served]) | Each system | No barcode - Track by location | Generic representation of sanitary drainage system.
Asset | D2020.10 | Not on One-Line | D2020 - Plumbing - Sanitary Drainage - Sewage Ejector Pump | D2020 - Plumbing - Sanitary Drainage | Sewage Ejector Pump |  | D. Plumbing - Sanitary Drainage - Sewage Ejector Pump | D. Plumbing - Sanitary Drainage | Sewage Ejector Pump |  | Sewage Ejector Pump | Each pump set | Barcode on control panels | This is a pump system that receives waste water from various plumbing fixtures and ejects it to the city sewer system. Normally installed where the city sewer system is above the plumbing fixture thus requiring the waste to be lifted via pumping action.. |  | 21-04 20 20 10 | Sanitary Sewerage Equipment | 22-22 13 29 | Sanitary Sewerage Pumps | 23-27 17 35 | Sewage Ejectors
Asset | D2020.30 | Not on One-Line | D2020 - Plumbing - Sanitary Drainage - Grease Trap | D2020 - Plumbing - Sanitary Drainage | Grease Trap |  | D. Plumbing - Sanitary Drainage - Grease Trap | D. Plumbing - Sanitary Drainage | Grease Trap |  | Grease Trap | Each trap | Tracked by room | A plumbing device designed to intercept most greases and solids before they enter the facilities wastewater disposal system |  | 21-04 20 20 90 | Sanitary Drainage Supplementary Components | 22-22 13 19 23 | Fats, Oils, and Grease Disposal Systems | 23-39 33 17 15 | Grease Traps
Asset | D2020.30 | Not on One-Line | D2020 - Plumbing - Sanitary Drainage - Interceptors Sediment/Plaster | D2020 - Plumbing - Sanitary Drainage | Interceptors Sediment/Plaster |  | D. Plumbing - Sanitary Drainage - Interceptors Sediment/Plaster | D. Plumbing - Sanitary Drainage | Interceptors Sediment/Plaster |  | Interceptors Sediment/Plaster | Each trap | Tracked by room | A vessel built-in under a basin to provide a strainer in the draining system. Leftover plaster is filtered off when the tools are cleaned. |  | 21-04 20 20 90 | Sanitary Drainage Supplementary Components | 22-46 46 00 | Sediment Removal Equipment | 23-27 55 35 | Liquid Separators
Supplemental Elements | D2020.99 | n/a | D2020 - Plumbing - Sanitary Drainage - [Supplemental Elements] Sanitary Drainage | D2020 - Plumbing - Sanitary Drainage | [Supplemental Elements] Sanitary Drainage |  | D. Plumbing - Sanitary Drainage - [Supplemental Elements] Sanitary Drainage | D. Plumbing - Sanitary Drainage | [Supplemental Elements] Sanitary Drainage |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2030 |  | D2030 - Plumbing - Other Drainage | D2030 - Plumbing - Other Drainage |  |  | D. Plumbing - Other Drainage | D. Plumbing - Other Drainage | [5 empty] | General Category |  | 21-04 20 30 | Building Support Plumbing Systems | 22-22 14 00
Asset | D2030.10 | Not on One-Line | D2030 - Plumbing - Other Drainage - Storm Emergency Pump | D2030 - Plumbing - Other Drainage | Storm Emergency Pump |  | D. Plumbing - Other Drainage - Storm Emergency Pump | D. Plumbing - Other Drainage | Storm Emergency Pump |  | Storm Emergency Pump | Each pump set | On control panel | An ejector pump, often gas or diesel driven used to supplement the installed pump capacity. May be fixed or mobile. |  | 21-04 20 30 10 | Stormwater Drainage Equipment | 22-33 45 00 | Storm Utility Drainage Pumps | 23-27 17 00 | Pumps
Asset | D2030.10 | Not on One-Line | D2030 - Plumbing - Other Drainage - Sump Pump | D2030 - Plumbing - Other Drainage | Sump Pump |  | D. Plumbing - Other Drainage - Sump Pump | D. Plumbing - Other Drainage | Sump Pump |  | Sump Pump | Each pump set | On control panel | Pump typically found at the lowest level of a building designed to dewater spaces from storm and ground water intrusion |  | 21-04 20 30 10 | Stormwater Drainage Equipment | 22-22 14 29 | Sump Pumps | 23-27 17 00 | Pumps
Supplemental Elements | D2030.10.99 | n/a | D2030 - Plumbing - Other Drainage - [Supplemental Elements] Other Drainage | D2030 - Plumbing - Other Drainage | [Supplemental Elements] Other Drainage |  | D. Plumbing - Other Drainage - [Supplemental Elements] Other Drainage | D. Plumbing - Other Drainage | [Supplemental Elements] Other Drainage |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2050 |  | D2050 - Plumbing - Control Air | D2050 - Plumbing - Control Air |  |  | D. Plumbing - Control Air | D. Plumbing - Control Air | [5 empty] | General Category |  | 21-04 20 60 | Process Support Plumbing Systems | 22-22 60 00 | Gas and Vacuum Systems for Laboratory and Healthcare Facilities
System | D2050 | Not on One-Line | D2050 - Plumbing - Control Air - (System) Control Air | D2050 - Plumbing - Control Air | (System) Control Air |  | D. Plumbing - Control Air - (System) Control Air | D. Plumbing - Control Air | (System) Control Air |  | SYS Control Air ([Area Served]) | Each system | No barcode - Track by location | Generic representation of Control Air System
Asset | D2050 | Not on One-Line | D2050 - Plumbing - Control Air - Control Air Compressor | D2050 - Plumbing - Control Air | Control Air Compressor |  | D. Plumbing - Control Air - Control Air Compressor | D. Plumbing - Control Air | Control Air Compressor |  | Control Air Compressor | Each compressor unit | On control panel | Air compressor designed to deliver compressed air for pneumatic controls (e.g. damper or valve actuators). |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-27 21 00 | Compressors
Asset | D2050 | Not on One-Line | D2050 - Plumbing - Control Air - Control Air Dryer | D2050 - Plumbing - Control Air | Control Air Dryer |  | D. Plumbing - Control Air - Control Air Dryer | D. Plumbing - Control Air | Control Air Dryer |  | Control Air Dryer | Each dryer unit (only if standalone, otherwise this is part of Control Air Compressor) | On control panel | Device that removes excessive moisture content from compressed air. Typically tracked as part of the Control Air Compressor. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-33 47 00 | Air Dryers
Asset | D2050 | Not on One-Line | D2050 - Plumbing - Control Air - Control Air Receiver | D2050 - Plumbing - Control Air | Control Air Receiver |  | D. Plumbing - Control Air - Control Air Receiver | D. Plumbing - Control Air | Control Air Receiver |  | Control Air Receiver | Each air receiver unit (only if standalone, otherwise this is part of Control Air Compressor) | On control panel | A reservoir vessel that stores high pressure air produced in the compressor. Typically tracked as part of the Control Air Compressor. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-25 33 19 | Medical Gas Delivery Columns
Supplemental Elements | D2050.99 | n/a | D2050 - Plumbing - Control Air - [Supplemental Elements] Control Air | D2050 - Plumbing - Control Air | [Supplemental Elements] Control Air |  | D. Plumbing - Control Air - [Supplemental Elements] Control Air | D. Plumbing - Control Air | [Supplemental Elements] Control Air |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.10a |  | D2060.10 - Plumbing - Lab Air | D2060.10 - Plumbing - Lab Air |  |  | D. Plumbing - Lab Air | D. Plumbing - Lab Air | [5 empty] | General Category |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 00 | Compressed-Air Systems for Laboratory and Healthcare Facilities | 23-25 33 00 | Medical Gas Products
System | D2060.10a | D20-2 | D2060.10 - Plumbing - Lab Air - (System) Laboratory Air | D2060.10 - Plumbing - Lab Air | (System) Laboratory Air |  | D. Plumbing - Lab Air - (System) Laboratory Air | D. Plumbing - Lab Air | (System) Laboratory Air |  | SYS Lab Air ([Area Served]) | Generic asset for Laboratory Air System | Track by area served | This is a general category for the Laboratory Air System and is meant to track data for this system that cannot otherwise be tracked by an asset within the system. For example, hangers, piping, labeling, modifications, etc. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 53 | Laboratory Compressed-Air Equipment
Asset | D2060.10a | D20-2 | D2060.10 - Plumbing - Lab Air - Compressor - Laboratory Air | D2060.10 - Plumbing - Lab Air | Compressor - Laboratory Air |  | D. Plumbing - Lab Air - Compressor - Laboratory Air | D. Plumbing - Lab Air | Compressor - Laboratory Air |  | Compressor - Laboratory Air | Each compressor | On control panel | Specialized air compressor designed to deliver compressed air for lab purposes. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 53 | Laboratory Compressed-Air Equipment | 23-27 21 00 | Compressors
Asset | D2060.10a | D20-2 | D2060.10 - Plumbing - Lab Air - Dryer - Laboratory Air | D2060.10 - Plumbing - Lab Air | Dryer - Laboratory Air |  | D. Plumbing - Lab Air - Dryer - Laboratory Air | D. Plumbing - Lab Air | Dryer - Laboratory Air |  | Dryer - Laboratory Air | Each dryer | On control panel | This is a device that removes excessive moisture content from Laboratory Air. Can be refrigerated or desiccant. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 53 | Laboratory Compressed-Air Equipment | 23-33 47 00 | Air Dryers
Supplemental Elements | D2060.10a.99 | n/a | D2060.10 - Plumbing - Lab Air - [Supplemental Elements] Lab Air | D2060.10 - Plumbing - Lab Air | [Supplemental Elements] Lab Air |  | D. Plumbing - Lab Air - [Supplemental Elements] Lab Air | D. Plumbing - Lab Air | [Supplemental Elements] Lab Air |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.10b |  | D2060.10 - Plumbing - Medical Air | D2060.10 - Plumbing - Medical Air |  |  | D. Plumbing - Medical Air | D. Plumbing - Medical Air | [5 empty] | General Category |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 00 | Compressed-Air Systems for Laboratory and Healthcare Facilities | 23-25 33 00 | Medical Gas Products
System | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - (System) Medical Air | D2060.10 - Plumbing - Medical Air | (System) Medical Air |  | D. Plumbing - Medical Air - (System) Medical Air | D. Plumbing - Medical Air | (System) Medical Air |  | SYS Med Air ([Area Served]) | Generic asset for Medical Air System | Track by area served | This is a general category for the Medical Air System and is meant to track data for this system that cannot otherwise be track by an asset within the system. For example, hangers, piping, labeling, modifications, etc. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Compressor - Medical Air | D2060.10 - Plumbing - Medical Air | Compressor - Medical Air |  | D. Plumbing - Medical Air - Compressor - Medical Air | D. Plumbing - Medical Air | Compressor - Medical Air |  | Compressor - Medical Air | Each compressor | On control panel | A compressor that is designed to exclude oil from the air stream and compression chamber and that does not under normal operating conditions or any single fault add any toxic or flammable contaminants to the compressed air. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-27 21 00 | Compressors
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Dryer - Medical Air | D2060.10 - Plumbing - Medical Air | Dryer - Medical Air |  | D. Plumbing - Medical Air - Dryer - Medical Air | D. Plumbing - Medical Air | Dryer - Medical Air |  | Dryer - Medical Air | Each dryer | On control panel | This is a device that removes excessive moisture content from Medical Air. Can be refrigerated or desiccant. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-33 47 00 | Air Dryers
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Main Valve - Medical Air | D2060.10 - Plumbing - Medical Air | Main Valve - Medical Air |  | D. Plumbing - Medical Air - Main Valve - Medical Air | D. Plumbing - Medical Air | Main Valve - Medical Air |  | Main Valve - Medical Air ([Area Served]) | Each valve | On or near identification plate if possible or back of valve tag. | This is a valve connected to the entire distribution system and is used to shut down the system when the source valve is not accessible. A Main Valve - Medical Air is installed upstream of the Source Valve - Medical Air outside the room where the source equipment is. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Outlet - Medical Air | D2060.10 - Plumbing - Medical Air | Outlet - Medical Air |  | D. Plumbing - Medical Air - Outlet - Medical Air | D. Plumbing - Medical Air | Outlet - Medical Air |  | Outlet - Medical Air | Each outlet station | On or near identification plate if possible or back of valve tag. | An outlet point in a piped Medical Air distribution system at which the user makes connections and disconnections. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-25 33 25 | Medical Gas Outlets
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Receiver - Medical Air | D2060.10 - Plumbing - Medical Air | Receiver - Medical Air |  | D. Plumbing - Medical Air - Receiver - Medical Air | D. Plumbing - Medical Air | Receiver - Medical Air |  | Receiver - Medical Air | Each receiver | On tank | A reservoir vessel that stores high pressure air produced in the compressor. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-25 33 19 | Medical Gas Delivery Columns
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Riser Valve - Medical Air | D2060.10 - Plumbing - Medical Air | Riser Valve - Medical Air |  | D. Plumbing - Medical Air - Riser Valve - Medical Air | D. Plumbing - Medical Air | Riser Valve - Medical Air |  | Riser Valve - Medical Air ([Area Served]) | Each valve | On or near identification plate if possible or back of valve tag. | This valve is installed to allow the entire Medical Air riser to be shut down without impacting the rest of the facility. A Riser Valve - Medical Air is place in the Medical Air riser adjacent to the main line. This valve is installed downstream of the Main Valve - Medical Air. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Service Valve - Medical Air | D2060.10 - Plumbing - Medical Air | Service Valve - Medical Air |  | D. Plumbing - Medical Air - Service Valve - Medical Air | D. Plumbing - Medical Air | Service Valve - Medical Air |  | Service Valve - Medical Air ([Area Served]) | Each valve | On or near identification plate if possible or back of valve tag. | A valve to allow servicing or modification of lateral branch piping from a main or riser without shutting down the entire main, rise, or facility. It is installed upstream of a Riser Valve - Medical Air. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Source Valve - Medical Air | D2060.10 - Plumbing - Medical Air | Source Valve - Medical Air |  | D. Plumbing - Medical Air - Source Valve - Medical Air | D. Plumbing - Medical Air | Source Valve - Medical Air |  | Source Valve - Medical Air ([Area Served]) | Each valve | On or near identification plate if possible or back of valve tag. | This valve allows the entire source, including all accessory devices to be isolated from the facility. It is placed at the immediate connection of the Medical Air System. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.10b | D20-3 | D2060.10 - Plumbing - Medical Air - Zone Valve - Medical Air | D2060.10 - Plumbing - Medical Air | Zone Valve - Medical Air |  | D. Plumbing - Medical Air - Zone Valve - Medical Air | D. Plumbing - Medical Air | Zone Valve - Medical Air |  | Zone Valve - Medical Air ([Area Served]) | Each valve | On identification plate if possible, back of valve tag, on zone valve box above valve | A valve to allow servicing or modification to the distribution piping or Medical Gas Outlets - Medical Air. This valve is installed on wall in the nurse’s stations to allow for easy access in case of a fire or other emergency and is upstream of a Service Valve - Medical Air. |  | 21-04 20 60 10 | Compressed-Air Systems | 22-22 61 19 70 | Healthcare Compressed-Air Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Supplemental Elements | D2060.10b.99 | n/a | D2060.10 - Plumbing - Medical Air - [Supplemental Elements] Medical Air | D2060.10 - Plumbing - Medical Air | [Supplemental Elements] Medical Air |  | D. Plumbing - Medical Air - [Supplemental Elements] Medical Air | D. Plumbing - Medical Air | [Supplemental Elements] Medical Air |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.20a |  | D2060.20 - Plumbing - Lab Vacuum | D2060.20 - Plumbing - Lab Vacuum |  |  | D. Plumbing - Lab Vacuum | D. Plumbing - Lab Vacuum | [5 empty] | General Category |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 00
System | D2060.20a | Not on One-Line | D2060.20 - Plumbing - Lab Vacuum - (System) Laboratory Vacuum | D2060.20 - Plumbing - Lab Vacuum | (System) Laboratory Vacuum |  | D. Plumbing - Lab Vacuum - (System) Laboratory Vacuum | D. Plumbing - Lab Vacuum | (System) Laboratory Vacuum |  | SYS Lab Vacuum ([Area Served]) | Generic asset for Laboratory Vacuum System | Track by area served | A dedicated system, used in laboratories, with central pumps connected to a piping system running to point of use outlets. The pumps induce a negative pressure in relation to the ambient environment. Devices are attached via hoses to the outlet allowing evacuation of fluids or other needs. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment
Asset | D2060.20a | Not on One-Line | D2060.20 - Plumbing - Lab Vacuum - Pump - Laboratory Vacuum | D2060.20 - Plumbing - Lab Vacuum | Pump - Laboratory Vacuum |  | D. Plumbing - Lab Vacuum - Pump - Laboratory Vacuum | D. Plumbing - Lab Vacuum | Pump - Laboratory Vacuum |  | Pump - Laboratory Vacuum | Each pump | On control panel | Specialized vacuum pump designed to pull vacuum for lab purposes. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-27 17 00 | Pumps
Supplemental Elements | D2060.20a.99 | n/a | D2060.20 - Plumbing - Lab Vacuum - [Supplemental Elements] Lab Vacuum | D2060.20 - Plumbing - Lab Vacuum | [Supplemental Elements] Lab Vacuum |  | D. Plumbing - Lab Vacuum - [Supplemental Elements] Lab Vacuum | D. Plumbing - Lab Vacuum | [Supplemental Elements] Lab Vacuum |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.20b |  | D2060.20 - Plumbing - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum |  |  | D. Plumbing - Medical Vacuum | D. Plumbing - Medical Vacuum | [5 empty] | General Category |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 00
System | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - (System) Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | (System) Medical Vacuum |  | D. Plumbing - Medical Vacuum - (System) Medical Vacuum | D. Plumbing - Medical Vacuum | (System) Medical Vacuum |  | SYS Med Vacuum ([Area Served]) | Generic asset for Medical Air System | Track by area served | A dedicated system, used in healthcare, with central pumps connected to a piping system running to point of use outlets. The pumps induce a negative pressure in relation to the ambient environment. Devices are attached via hoses to the outlet allowing evacuation of fluids or other needs.
Asset | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - Main Valve - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | Main Valve - Medical Vacuum |  | D. Plumbing - Medical Vacuum - Main Valve - Medical Vacuum | D. Plumbing - Medical Vacuum | Main Valve - Medical Vacuum |  | Main Valve - Medical Vacuum ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | A valve that is connected to the entire distribution system and is used to shut down the system when the source valve is not accessible. A Main Valve - Medical Vacuum is installed upstream of the Source Valve - Medical Vacuum outside the room where the source equipment is. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - Outlet - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | Outlet - Medical Vacuum |  | D. Plumbing - Medical Vacuum - Outlet - Medical Vacuum | D. Plumbing - Medical Vacuum | Outlet - Medical Vacuum |  | Outlet - Medical Vacuum | Each outlet station | On cover plate. | An outlet point in a piped Medical Vacuum System at which the user makes connections and disconnections. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-25 33 25 | Medical Gas Outlets
Asset | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - Pump - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | Pump - Medical Vacuum |  | D. Plumbing - Medical Vacuum - Pump - Medical Vacuum | D. Plumbing - Medical Vacuum | Pump - Medical Vacuum |  | Pump - Medical Vacuum | Each pump | On control panel | Specialized vacuum pump designed to pull vacuum for medical purposes. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-27 17 00 | Pumps
Asset | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - Riser Valve - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | Riser Valve - Medical Vacuum |  | D. Plumbing - Medical Vacuum - Riser Valve - Medical Vacuum | D. Plumbing - Medical Vacuum | Riser Valve - Medical Vacuum |  | Riser Valve - Medical Vacuum ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow the entire Medical Vacuum riser to be shut down without impacting the rest of the facility. A Riser Valve - Medical Vacuum is place in the Medical Vacuum riser adjacent to the main line. This valve is installed downstream of the Main Valve - Medical Vacuum. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - Service Valve - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | Service Valve - Medical Vacuum |  | D. Plumbing - Medical Vacuum - Service Valve - Medical Vacuum | D. Plumbing - Medical Vacuum | Service Valve - Medical Vacuum |  | Service Valve - Medical Vacuum ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow servicing or modification of lateral branch piping from a main or riser without shutting down the entire main, rise, or facility. A Service Valve - Medical Vacuum is installed upstream of a Riser Valve - Medical Vacuum. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - Source Valve - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | Source Valve - Medical Vacuum |  | D. Plumbing - Medical Vacuum - Source Valve - Medical Vacuum | D. Plumbing - Medical Vacuum | Source Valve - Medical Vacuum |  | Source Valve - Medical Vacuum ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve allows the entire source, including all accessory devices to be isolated from the facility. A Source Valve - Medical Vacuum is place at the immediate connection of the Medical Vacuum system. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - Tank - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | Tank - Medical Vacuum |  | D. Plumbing - Medical Vacuum - Tank - Medical Vacuum | D. Plumbing - Medical Vacuum | Tank - Medical Vacuum |  | Tank - Medical Vacuum ([Area Served]) | Each tank | On tank | The tank is a reservoir vessel upon which the associated pumps pull a vacuum. It maintains the negative pressure for vacuum suction between pump cycles. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-27 29 15 | Specialized Tanks
Asset | D2060.20b | D20-4 | D2060.20 - Plumbing - Medical Vacuum - Zone Valve - Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | Zone Valve - Medical Vacuum |  | D. Plumbing - Medical Vacuum - Zone Valve - Medical Vacuum | D. Plumbing - Medical Vacuum | Zone Valve - Medical Vacuum |  | Zone Valve - Medical Vacuum ([Area Served]) | Each valve | On identification plate if possible, back of valve tag, on zone valve box above valve | This valve allows servicing or modification to the distribution piping or Medical Gas Outlets - MV. A Zone Valve - Medical Vacuum is installed upstream of a Service Valve - Medical Vacuum. This valve is installed on wall in the nurse’s stations to allow for easy access in case of a fire or other emergency. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 19 70 | Healthcare Vacuum Equipment | 23-25 33 29 | Medical Gas Shutoff Valves
Supplemental Elements | D2060.20b.99 | n/a | D2060.20 - Plumbing - Medical Vacuum - [Supplemental Elements] Medical Vacuum | D2060.20 - Plumbing - Medical Vacuum | [Supplemental Elements] Medical Vacuum |  | D. Plumbing - Medical Vacuum - [Supplemental Elements] Medical Vacuum | D. Plumbing - Medical Vacuum | [Supplemental Elements] Medical Vacuum |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.20c |  | D2060.20a - Plumbing - WAGD Vacuum | D2060.20a - Plumbing - WAGD Vacuum |  |  | D. Plumbing - WAGD Vacuum | D. Plumbing - WAGD Vacuum | [5 empty] | General Category |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 |  | 23-25 11 13 23 11 | Anesthesia Inhalation Analgesia Central Gases and Vacuum Units
System | D2060.20c | D20-5 | D2060.20a - Plumbing - WAGD Vacuum - (System) Waste Anesthesia Gas Disposal | D2060.20a - Plumbing - WAGD Vacuum | (System) Waste Anesthesia Gas Disposal |  | D. Plumbing - WAGD Vacuum - (System) Waste Anesthesia Gas Disposal | D. Plumbing - WAGD Vacuum | (System) Waste Anesthesia Gas Disposal |  | SYS WAGD ([Area Served]) | Generic asset for WAGD System | Track by area served | A dedicated medical system with central pumps connected to a piping system running to point of use outlets. The pumps induce a negative pressure in relation to the ambient environment. Waste anesthesia gases are drawn into the system and discharged outside the building. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 23 | Waste Anesthesia-Gas Piping | 23-25 33 31 | Medical Gas Treatment Equipment
Asset | D2060.20c | D20-5 | D2060.20a - Plumbing - WAGD Vacuum - Blower - Waste Anesthesia Gas Disposal | D2060.20a - Plumbing - WAGD Vacuum | Blower - Waste Anesthesia Gas Disposal |  | D. Plumbing - WAGD Vacuum - Blower - Waste Anesthesia Gas Disposal | D. Plumbing - WAGD Vacuum | Blower - Waste Anesthesia Gas Disposal |  | Blower - WAGD | Each blower | On blower | A low pressure moderate volume vacuum pump centrally located that is utilized in a waste anesthesia system |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 23 | Waste Anesthesia-Gas Piping
Asset | D2060.20c | D20-5 | D2060.20a - Plumbing - WAGD Vacuum - Main Valve - Waste Anesthesia Gas Disposal | D2060.20a - Plumbing - WAGD Vacuum | Main Valve - Waste Anesthesia Gas Disposal |  | D. Plumbing - WAGD Vacuum - Main Valve - Waste Anesthesia Gas Disposal | D. Plumbing - WAGD Vacuum | Main Valve - Waste Anesthesia Gas Disposal |  | Main Valve - WAGD ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | A valve that is connected to the entire distribution system and is used to shut down the system when the source valve is not accessible. A Main Valve - Waste Anesthesia Gas Disposal is installed upstream of the Source Valve - Waste Anesthesia Gas Disposal outside the room where the source equipment is. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 23 | Waste Anesthesia-Gas Piping | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.20c | D20-5 | D2060.20a - Plumbing - WAGD Vacuum - Outlet - Waste Anesthesia Gas Disposal | D2060.20a - Plumbing - WAGD Vacuum | Outlet - Waste Anesthesia Gas Disposal |  | D. Plumbing - WAGD Vacuum - Outlet - Waste Anesthesia Gas Disposal | D. Plumbing - WAGD Vacuum | Outlet - Waste Anesthesia Gas Disposal |  | Outlet - WAGD | Each outlet station | On cover plate. | An outlet point in a piped Waste Anesthesia Gas Disposal System at which the user makes connections and disconnections. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 23 | Waste Anesthesia-Gas Piping | 23-25 33 25 | Medical Gas Outlets
Asset | D2060.20c | D20-5 | D2060.20a - Plumbing - WAGD Vacuum - Riser Valve - Waste Anesthesia Gas Disposal | D2060.20a - Plumbing - WAGD Vacuum | Riser Valve - Waste Anesthesia Gas Disposal |  | D. Plumbing - WAGD Vacuum - Riser Valve - Waste Anesthesia Gas Disposal | D. Plumbing - WAGD Vacuum | Riser Valve - Waste Anesthesia Gas Disposal |  | Riser Valve - WAGD ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow the entire Waste Anesthesia Gas Disposal riser to be shut down without impacting the rest of the facility. A Riser Valve - Waste Anesthesia Gas Disposal is placed in the Waste Anesthesia Gas Disposal riser adjacent to the main line. This valve is installed downstream of the Main Valve - Waste Anesthesia Gas Disposal. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 23 | Waste Anesthesia-Gas Piping | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.20c | D20-5 | D2060.20a - Plumbing - WAGD Vacuum - Service Valve - Waste Anesthesia Gas Disposal | D2060.20a - Plumbing - WAGD Vacuum | Service Valve - Waste Anesthesia Gas Disposal |  | D. Plumbing - WAGD Vacuum - Service Valve - Waste Anesthesia Gas Disposal | D. Plumbing - WAGD Vacuum | Service Valve - Waste Anesthesia Gas Disposal |  | Service Valve - WAGD ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow servicing or modification of lateral branch piping from a main or riser without shutting down the entire main, rise, or facility. A Service Valve - Waste Anesthesia Gas Disposal is installed upstream of a Riser Valve - Waste Anesthesia Gas Disposal. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 23 | Waste Anesthesia-Gas Piping | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.20c | D20-5 | D2060.20a - Plumbing - WAGD Vacuum - Source Valve - Waste Anesthesia Gas Disposal | D2060.20a - Plumbing - WAGD Vacuum | Source Valve - Waste Anesthesia Gas Disposal |  | D. Plumbing - WAGD Vacuum - Source Valve - Waste Anesthesia Gas Disposal | D. Plumbing - WAGD Vacuum | Source Valve - Waste Anesthesia Gas Disposal |  | Source Valve - WAGD ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve allows the entire source, including all accessory devices to be isolated from the facility. A Source Valve - Waste Anesthesia Gas Disposal is place at the immediate connection of the Waste Anesthesia Gas Disposal System. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 23 | Waste Anesthesia-Gas Piping | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.20c | D20-5 | D2060.20a - Plumbing - WAGD Vacuum - Zone Valve - Waste Anesthesia Gas Disposal | D2060.20a - Plumbing - WAGD Vacuum | Zone Valve - Waste Anesthesia Gas Disposal |  | D. Plumbing - WAGD Vacuum - Zone Valve - Waste Anesthesia Gas Disposal | D. Plumbing - WAGD Vacuum | Zone Valve - Waste Anesthesia Gas Disposal |  | Zone Valve - WAGD ([Area Served]) | Each valve | On identification plate if possible, back of valve tag, on zone valve box above valve | This valve allows servicing or modification to the distribution piping or Medical Gas Outlets - WAGD. A Zone Valve - Waste Anesthesia Gas Disposal is installed upstream of a Service Valve - Waste Anesthesia Gas Disposal. This valve is installed on wall in the nurse’s stations to allow for easy access in case of a fire or other emergency. |  | 21-04 20 60 20 | Vacuum Systems | 22-22 62 23 | Waste Anesthesia-Gas Piping | 23-25 33 29 | Medical Gas Shutoff Valves
Supplemental Elements | D2060.20c.99 | n/a | D2060.20a - Plumbing - WAGD Vacuum - [Supplemental Elements] WAGD | D2060.20a - Plumbing - WAGD Vacuum | [Supplemental Elements] WAGD |  | D. Plumbing - WAGD Vacuum - [Supplemental Elements] WAGD | D. Plumbing - WAGD Vacuum | [Supplemental Elements] WAGD |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.30 |  | D2060.30 - Plumbing - Gas Systems | D2060.30 - Plumbing - Gas Systems |  |  | D. Plumbing - Gas Systems | D. Plumbing - Gas Systems | [5 empty] | General Category |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities
Asset | D2060.30 | Not on One-Line | D2060.30 - Plumbing - Gas Systems - Multi-Gas Outlet Station | D2060.30 - Plumbing - Gas Systems | Multi-Gas Outlet Station |  | D. Plumbing - Gas Systems - Multi-Gas Outlet Station | D. Plumbing - Gas Systems | Multi-Gas Outlet Station |  | Multi-Gas Outlet Station | Each Station | On cover | A medical gas station consisting of more than one gas outlet. Can be in a common fixture or outlets closely mounted together. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30 | Not on One-Line | D2060.30 - Plumbing - Gas Systems - Zone Valve Box | D2060.30 - Plumbing - Gas Systems | Zone Valve Box |  | D. Plumbing - Gas Systems - Zone Valve Box | D. Plumbing - Gas Systems | Zone Valve Box |  | Zone Valve Box | Each shutoff valve cabinet | On box (not cover) | Box containing the valves of various medical gases in a given area. Are designed that the box's removable window cannot be replaced when any valve is closed. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Supplemental Elements | D2060.30.99 | n/a | D2060.30 - Plumbing - Gas Systems - [Supplemental Elements] Gas Systems | D2060.30 - Plumbing - Gas Systems | [Supplemental Elements] Gas Systems |  | D. Plumbing - Gas Systems - [Supplemental Elements] Gas Systems | D. Plumbing - Gas Systems | [Supplemental Elements] Gas Systems |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.30a |  | D2060.30a - Plumbing - Oxygen Gas | D2060.30a - Plumbing - Oxygen Gas |  |  | D. Plumbing - Oxygen Gas | D. Plumbing - Oxygen Gas | [5 empty] | General Category |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00
System | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - (System) Oxygen Gas | D2060.30a - Plumbing - Oxygen Gas | (System) Oxygen Gas |  | D. Plumbing - Oxygen Gas - (System) Oxygen Gas | D. Plumbing - Oxygen Gas | (System) Oxygen Gas |  | SYS Oxygen ([Area Served]) | Generic asset for Oxygen Gas System | Track by area served | This is a general category for the Oxygen System and is meant to track data for this system that can not otherwise be tracked by an asset within the system. For example, hangers, piping, labeling, modifications, etc. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 11 13 29 | Oxygen Delivery Products
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Bulk Storage - O2 | D2060.30a - Plumbing - Oxygen Gas | Bulk Storage - O2 |  | D. Plumbing - Oxygen Gas - Bulk Storage - O2 | D. Plumbing - Oxygen Gas | Bulk Storage - O2 |  | Bulk Storage - O2 | Enclosure that holds bulk storage in form of portable bottles | On tag chain hung from fitting. | Enclosure that holds bulk storage of O2. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 15 | Medical Gas Cylinder Carts
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Main Valve - O2 | D2060.30a - Plumbing - Oxygen Gas | Main Valve - O2 |  | D. Plumbing - Oxygen Gas - Main Valve - O2 | D. Plumbing - Oxygen Gas | Main Valve - O2 |  | Main Valve - O2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | A valve that is connected to the entire distribution system and is used to shut down the system when the source valve is not accessible. A Main Valve - Oxygen is installed upstream of the Source Valve - Oxygen outside the room where the source equipment is. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Outlet - O2 | D2060.30a - Plumbing - Oxygen Gas | Outlet - O2 |  | D. Plumbing - Oxygen Gas - Outlet - O2 | D. Plumbing - Oxygen Gas | Outlet - O2 |  | Outlet - O2 | Each outlet station | On cover plate. | An outlet point in a piped O2 system at which the user makes connections and disconnections. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 25 | Medical Gas Outlets
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Riser Valve - O2 | D2060.30a - Plumbing - Oxygen Gas | Riser Valve - O2 |  | D. Plumbing - Oxygen Gas - Riser Valve - O2 | D. Plumbing - Oxygen Gas | Riser Valve - O2 |  | Riser Valve - O2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow the entire Oxygen riser to be shut down without impacting the rest of the facility. A Riser Valve - Oxygen is placed in the Oxygen riser adjacent to the main line. This valve is installed downstream of the Main Valve - Oxygen. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Service Valve - O2 | D2060.30a - Plumbing - Oxygen Gas | Service Valve - O2 |  | D. Plumbing - Oxygen Gas - Service Valve - O2 | D. Plumbing - Oxygen Gas | Service Valve - O2 |  | Service Valve - O2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow servicing or modification of lateral branch piping from a main or riser without shutting down the entire main, rise, or facility. A Service Valve - Oxygen is installed upstream of a Riser Valve - Oxygen. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Source Valve - O2 | D2060.30a - Plumbing - Oxygen Gas | Source Valve - O2 |  | D. Plumbing - Oxygen Gas - Source Valve - O2 | D. Plumbing - Oxygen Gas | Source Valve - O2 |  | Source Valve - O2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve allows the entire source, including all accessory devices to be isolated from the facility. A Source Valve - Oxygen is place at the immediate connection of the Oxygen System. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Storage Tank - O2 | D2060.30a - Plumbing - Oxygen Gas | Storage Tank - O2 |  | D. Plumbing - Oxygen Gas - Storage Tank - O2 | D. Plumbing - Oxygen Gas | Storage Tank - O2 |  | Storage Tank - O2 ([Area Served]) | Each fixed storage vessel | On tank, next to nameplate. | This is a storage vessel that stores compressed O2 used for clinical purposes |  | 21-04 20 60 30 | Gas Systems | 22-22 63 19 70 | Healthcare Gas Storage Tanks | 23-25 11 13 29 | Oxygen Delivery Products
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Vaporizer - O2 | D2060.30a - Plumbing - Oxygen Gas | Vaporizer - O2 |  | D. Plumbing - Oxygen Gas - Vaporizer - O2 | D. Plumbing - Oxygen Gas | Vaporizer - O2 |  | Vaporizer - O2 | Each unit | On Unit | A device that uses ambient air to transfer heat to the liquid gas and by warming and controlling the pressure convert it to a gas for distribution. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 31 | Medical Gas Treatment Equipment
Asset | D2060.30a | D20-6 | D2060.30a - Plumbing - Oxygen Gas - Zone Valve - O2 | D2060.30a - Plumbing - Oxygen Gas | Zone Valve - O2 |  | D. Plumbing - Oxygen Gas - Zone Valve - O2 | D. Plumbing - Oxygen Gas | Zone Valve - O2 |  | Zone Valve - O2 ([Area Served]) | Each valve | On identification plate if possible, back of valve tag, on zone valve box above valve | This valve allows servicing or modification to the distribution piping or Medical Gas Outlets - O2. A Zone Valve - Oxygen is installed upstream of a Service Valve - Oxygen. This valve is installed on wall in the nurse’s stations to allow for easy access in case of a fire or other emergency. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Supplemental Elements | D2060.30a.99 | n/a | D2060.30a - Plumbing - Oxygen Gas - [Supplemental Elements] Oxygen Gas | D2060.30a - Plumbing - Oxygen Gas | [Supplemental Elements] Oxygen Gas |  | D. Plumbing - Oxygen Gas - [Supplemental Elements] Oxygen Gas | D. Plumbing - Oxygen Gas | [Supplemental Elements] Oxygen Gas |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.30b |  | D2060.30b - Plumbing - Nitrogen Gas | D2060.30b - Plumbing - Nitrogen Gas |  |  | D. Plumbing - Nitrogen Gas | D. Plumbing - Nitrogen Gas | [5 empty] | General Category |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00
System | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - (System) Nitrogen Gas | D2060.30b - Plumbing - Nitrogen Gas | (System) Nitrogen Gas |  | D. Plumbing - Nitrogen Gas - (System) Nitrogen Gas | D. Plumbing - Nitrogen Gas | (System) Nitrogen Gas |  | SYS Nitrogen ([Area Served]) | Generic asset for Nitrogen Gas System | Track by area served | This is a general category for the Nitrogen System and is meant to track data for this system that can not otherwise be tracked by an asset within the system. For example, hangers, piping, labeling, modifications, etc. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Bulk Storage - N2 | D2060.30b - Plumbing - Nitrogen Gas | Bulk Storage - N2 |  | D. Plumbing - Nitrogen Gas - Bulk Storage - N2 | D. Plumbing - Nitrogen Gas | Bulk Storage - N2 |  | Bulk Storage - N2 | Enclosure that holds bulk storage in form of portable bottles | On tag chain hung from fitting. | Enclosure that holds bulk storage of Nitrogen gas |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 15 | Medical Gas Cylinder Carts
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Main Valve - N2 | D2060.30b - Plumbing - Nitrogen Gas | Main Valve - N2 |  | D. Plumbing - Nitrogen Gas - Main Valve - N2 | D. Plumbing - Nitrogen Gas | Main Valve - N2 |  | Main Valve - N2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | A valve that is connected to the entire distribution system and is used to shut down the system when the source valve is not accessible. A Main Valve - Nitrogen is installed upstream of the Source Valve - Nitrogen outside the room where the source equipment is. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Manifold - N2 | D2060.30b - Plumbing - Nitrogen Gas | Manifold - N2 |  | D. Plumbing - Nitrogen Gas - Manifold - N2 | D. Plumbing - Nitrogen Gas | Manifold - N2 |  | Manifold - N2 | Each unit | On or next to ID Plate | An arrangement of piping and valves that connect one or more cylinders of gas to a building distribution system. Equipped with pressure regulation, pressure indication and automatic reserve changeover capability. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 23 | Medical Gas Manifolds
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Outlet - N2 | D2060.30b - Plumbing - Nitrogen Gas | Outlet - N2 |  | D. Plumbing - Nitrogen Gas - Outlet - N2 | D. Plumbing - Nitrogen Gas | Outlet - N2 |  | Outlet - N2 | Each outlet station | On cover plate. | An outlet point in a piped N2 system at which the user makes connections and disconnections. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 25 | Medical Gas Outlets
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Riser Valve - N2 | D2060.30b - Plumbing - Nitrogen Gas | Riser Valve - N2 |  | D. Plumbing - Nitrogen Gas - Riser Valve - N2 | D. Plumbing - Nitrogen Gas | Riser Valve - N2 |  | Riser Valve - N2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow the entire Nitrogen riser to be shut down without impacting the rest of the facility. A Riser Valve - Nitrogen is placed in the Nitrogen riser adjacent to the main line. This valve is installed downstream of the Main Valve - Nitrogen |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Service Valve - N2 | D2060.30b - Plumbing - Nitrogen Gas | Service Valve - N2 |  | D. Plumbing - Nitrogen Gas - Service Valve - N2 | D. Plumbing - Nitrogen Gas | Service Valve - N2 |  | Service Valve - N2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow servicing or modification of lateral branch piping from a main or riser without shutting down the entire main, rise, or facility. A Service Valve - Nitrogen is installed upstream of a Riser Valve - Nitrogen. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Source Valve - N2 | D2060.30b - Plumbing - Nitrogen Gas | Source Valve - N2 |  | D. Plumbing - Nitrogen Gas - Source Valve - N2 | D. Plumbing - Nitrogen Gas | Source Valve - N2 |  | Source Valve - N2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve allows the entire source, including all accessory devices to be isolated from the facility. A Source Valve - Nitrogen is place at the immediate connection of the Nitrogen System. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Vaporizer - N2 | D2060.30b - Plumbing - Nitrogen Gas | Vaporizer - N2 |  | D. Plumbing - Nitrogen Gas - Vaporizer - N2 | D. Plumbing - Nitrogen Gas | Vaporizer - N2 |  | Vaporizer - N2 | Each unit | On or next to ID Plate | A device that uses ambient air to transfer heat to the liquid gas and by warming and controlling the pressure convert it to a gas for distribution. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 31 | Medical Gas Treatment Equipment
Asset | D2060.30b | D20-7 | D2060.30b - Plumbing - Nitrogen Gas - Zone Valve - N2 | D2060.30b - Plumbing - Nitrogen Gas | Zone Valve - N2 |  | D. Plumbing - Nitrogen Gas - Zone Valve - N2 | D. Plumbing - Nitrogen Gas | Zone Valve - N2 |  | Zone Valve - N2 ([Area Served]) | Each valve | On identification plate if possible, back of valve tag, on zone valve box above valve | This valve allows servicing or modification to the distribution piping or Medical Gas Outlets - N2. A Zone Valve - Nitrogen is installed upstream of a Service Valve - Nitrogen. This valve is installed on wall in the nurse’s stations to allow for easy access in case of a fire or other emergency. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Supplemental Elements | D2060.30b.99 | n/a | D2060.30b - Plumbing - Nitrogen Gas - [Supplemental Elements] Nitrogen Gas | D2060.30b - Plumbing - Nitrogen Gas | [Supplemental Elements] Nitrogen Gas |  | D. Plumbing - Nitrogen Gas - [Supplemental Elements] Nitrogen Gas | D. Plumbing - Nitrogen Gas | [Supplemental Elements] Nitrogen Gas |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.30c |  | D2060.30c - Plumbing - Nitrous Oxide Gas | D2060.30c - Plumbing - Nitrous Oxide Gas |  |  | D. Plumbing - Nitrous Oxide Gas | D. Plumbing - Nitrous Oxide Gas | [5 empty] | General Category |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00
System | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - (System) Nitrous Oxide Gas | D2060.30c - Plumbing - Nitrous Oxide Gas | (System) Nitrous Oxide Gas |  | D. Plumbing - Nitrous Oxide Gas - (System) Nitrous Oxide Gas | D. Plumbing - Nitrous Oxide Gas | (System) Nitrous Oxide Gas |  | SYS Nitrous Oxide ([Area Served]) | Generic asset for Nitrous Oxide Gas System | Track by area served | This is a general category for the Nitrous Oxide system and is meant to track data for this system that can not otherwise be tracked by an asset within the system. For example, hangers, piping, labeling, modifications, etc. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Bulk Storage - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Bulk Storage - N2O |  | D. Plumbing - Nitrous Oxide Gas - Bulk Storage - N2O | D. Plumbing - Nitrous Oxide Gas | Bulk Storage - N2O |  | Bulk Storage - N2O | Enclosure that holds bulk storage in form of portable bottles | On tag chain hung from fitting. | Enclosure that holds bulk storage of NOx gas. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 15 | Medical Gas Cylinder Carts
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Main Valve - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Main Valve - N2O |  | D. Plumbing - Nitrous Oxide Gas - Main Valve - N2O | D. Plumbing - Nitrous Oxide Gas | Main Valve - N2O |  | Main Valve - N2O ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | A valve that is connected to the entire distribution system and is used to shut down the system when the source valve is not accessible. A Main Valve - Nitrous Oxide is installed upstream of the Source Valve - Nitrous Oxide outside the room where the source equipment is. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Manifold - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Manifold - N2O |  | D. Plumbing - Nitrous Oxide Gas - Manifold - N2O | D. Plumbing - Nitrous Oxide Gas | Manifold - N2O |  | Manifold - N2O | Each unit | On or next to ID Plate | An arrangement of piping and valves that connect one or more cylinders of gas to a building distribution system. Equipped with pressure regulation, pressure indication and automatic reserve changeover capability. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 23 | Medical Gas Manifolds
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Outlet - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Outlet - N2O |  | D. Plumbing - Nitrous Oxide Gas - Outlet - N2O | D. Plumbing - Nitrous Oxide Gas | Outlet - N2O |  | Outlet - N2O | Each outlet station | On plate cover. | An outlet point in a piped N2O system at which the user makes connections and disconnections. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 25 | Medical Gas Outlets
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Riser Valve - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Riser Valve - N2O |  | D. Plumbing - Nitrous Oxide Gas - Riser Valve - N2O | D. Plumbing - Nitrous Oxide Gas | Riser Valve - N2O |  | Riser Valve - N2O ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow the entire Nitrous Oxide riser to be shut down without impacting the rest of the facility. A Riser Valve - Nitrous Oxide is placed in the Nitrogen riser adjacent to the main line. This valve is installed downstream of the Main Valve - Nitrous Oxide |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Service Valve - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Service Valve - N2O |  | D. Plumbing - Nitrous Oxide Gas - Service Valve - N2O | D. Plumbing - Nitrous Oxide Gas | Service Valve - N2O |  | Service Valve - N2O ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow servicing or modification of lateral branch piping from a main or riser without shutting down the entire main, rise, or facility. A Service Valve - Nitrous Oxide is installed upstream of a Riser Valve - Nitrous Oxide. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Source Valve - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Source Valve - N2O |  | D. Plumbing - Nitrous Oxide Gas - Source Valve - N2O | D. Plumbing - Nitrous Oxide Gas | Source Valve - N2O |  | Source Valve - N2O ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve allows the entire source, including all accessory devices to be isolated from the facility. A Source Valve - Nitrous Oxide is place at the immediate connection of the Nitrous Oxide System. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Vaporizer - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Vaporizer - N2O |  | D. Plumbing - Nitrous Oxide Gas - Vaporizer - N2O | D. Plumbing - Nitrous Oxide Gas | Vaporizer - N2O |  | Vaporizer - N2O | Each unit | On or next to ID Plate | A device that uses ambient air to transfer heat to the liquid gas and by warming and controlling the pressure convert it to a gas for distribution. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 31 | Medical Gas Treatment Equipment
Asset | D2060.30c | D20-8 | D2060.30c - Plumbing - Nitrous Oxide Gas - Zone Valve - N2O | D2060.30c - Plumbing - Nitrous Oxide Gas | Zone Valve - N2O |  | D. Plumbing - Nitrous Oxide Gas - Zone Valve - N2O | D. Plumbing - Nitrous Oxide Gas | Zone Valve - N2O |  | Zone Valve - N2O ([Area Served]) | Each valve | On identification plate if possible, back of valve tag, on zone valve box above valve | This valve allows servicing or modification to the distribution piping or Medical Gas Outlets - N2O. A Zone Valve - Nitrous Oxide is installed upstream of a Service Valve - Nitrous Oxide. This valve is installed on wall in the nurse’s stations to allow for easy access in case of a fire or other emergency. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Supplemental Elements | D2060.30c.99 | n/a | D2060.30c - Plumbing - Nitrous Oxide Gas - [Supplemental Elements] Nitrous Oxide Gas | D2060.30c - Plumbing - Nitrous Oxide Gas | [Supplemental Elements] Nitrous Oxide Gas |  | D. Plumbing - Nitrous Oxide Gas - [Supplemental Elements] Nitrous Oxide Gas | D. Plumbing - Nitrous Oxide Gas | [Supplemental Elements] Nitrous Oxide Gas |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.30d |  | D2060.30d - Plumbing - Carbon Dioxide Gas | D2060.30d - Plumbing - Carbon Dioxide Gas |  |  | D. Plumbing - Carbon Dioxide Gas | D. Plumbing - Carbon Dioxide Gas | [5 empty] | General Category |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00
System | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - (System) Carbon Dioxide Gas | D2060.30d - Plumbing - Carbon Dioxide Gas | (System) Carbon Dioxide Gas |  | D. Plumbing - Carbon Dioxide Gas - (System) Carbon Dioxide Gas | D. Plumbing - Carbon Dioxide Gas | (System) Carbon Dioxide Gas |  | SYS Carbon Dioxide ([Area Served]) | Generic asset for Carbon Dioxide Gas System | Track by area served | This is a general category for the Carbon Dioxide System and is meant to track data for this system that can not otherwise be tracked by an asset within the system. For example, hangers, piping, labeling, modifications, etc. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities
Asset | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - Bulk Storage - CO2 | D2060.30d - Plumbing - Carbon Dioxide Gas | Bulk Storage - CO2 |  | D. Plumbing - Carbon Dioxide Gas - Bulk Storage - CO2 | D. Plumbing - Carbon Dioxide Gas | Bulk Storage - CO2 |  | Bulk Storage - CO2 | Each condenser | On vessel | Enclosure and cylinders that store CO2 gas. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 15 | Medical Gas Cylinder Carts
Asset | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - Main Valve - CO2 | D2060.30d - Plumbing - Carbon Dioxide Gas | Main Valve - CO2 |  | D. Plumbing - Carbon Dioxide Gas - Main Valve - CO2 | D. Plumbing - Carbon Dioxide Gas | Main Valve - CO2 |  | Main Valve - CO2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | A valve that is connected to the entire distribution system and is used to shut down the system when the source valve is not accessible. A Main Valve - Carbon Dioxide is installed upstream of the Source Valve - Carbon Dioxide outside the room where the source equipment is. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - Manifold - CO2 | D2060.30d - Plumbing - Carbon Dioxide Gas | Manifold - CO2 |  | D. Plumbing - Carbon Dioxide Gas - Manifold - CO2 | D. Plumbing - Carbon Dioxide Gas | Manifold - CO2 |  | Manifold - CO2 | Each unit | On or next to ID Plate | An arrangement of piping and valves that connect one or more cylinders of gas to a building distribution system. Equipped with pressure regulation, pressure indication and automatic reserve changeover capability. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 23 | Medical Gas Manifolds
Asset | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - Outlet - CO2 | D2060.30d - Plumbing - Carbon Dioxide Gas | Outlet - CO2 |  | D. Plumbing - Carbon Dioxide Gas - Outlet - CO2 | D. Plumbing - Carbon Dioxide Gas | Outlet - CO2 |  | Outlet - CO2 | Each outlet station | On identification plate if possible or back of valve tag. | An outlet point in a piped CO2 system at which the user makes connections and disconnections. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 25 | Medical Gas Outlets
Asset | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - Riser Valve - CO2 | D2060.30d - Plumbing - Carbon Dioxide Gas | Riser Valve - CO2 |  | D. Plumbing - Carbon Dioxide Gas - Riser Valve - CO2 | D. Plumbing - Carbon Dioxide Gas | Riser Valve - CO2 |  | Riser Valve - CO2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow the entire Carbon Dioxide riser to be shut down without impacting the rest of the facility. A Riser Valve - Carbon Dioxide is placed in the Carbon Dioxide riser adjacent to the main line. This valve is installed downstream of the Main Valve - Carbon Dioxide. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - Service Valve - CO2 | D2060.30d - Plumbing - Carbon Dioxide Gas | Service Valve - CO2 |  | D. Plumbing - Carbon Dioxide Gas - Service Valve - CO2 | D. Plumbing - Carbon Dioxide Gas | Service Valve - CO2 |  | Service Valve - CO2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve is installed to allow servicing or modification of lateral branch piping from a main or riser without shutting down the entire main, rise, or facility. A Service Valve - Carbon Dioxide is installed upstream of a Riser Valve - Carbon Dioxide. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - Source Valve - CO2 | D2060.30d - Plumbing - Carbon Dioxide Gas | Source Valve - CO2 |  | D. Plumbing - Carbon Dioxide Gas - Source Valve - CO2 | D. Plumbing - Carbon Dioxide Gas | Source Valve - CO2 |  | Source Valve - CO2 ([Area Served]) | Each valve | On identification plate if possible or back of valve tag. | This valve allows the entire source, including all accessory devices to be isolated from the facility. A Source Valve - Carbon Dioxide is place at the immediate connection of the Carbon Dioxide System. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Asset | D2060.30d | D20-9 | D2060.30d - Plumbing - Carbon Dioxide Gas - Zone Valve - CO2 | D2060.30d - Plumbing - Carbon Dioxide Gas | Zone Valve - CO2 |  | D. Plumbing - Carbon Dioxide Gas - Zone Valve - CO2 | D. Plumbing - Carbon Dioxide Gas | Zone Valve - CO2 |  | Zone Valve - CO2 ([Area Served]) | Each valve | On identification plate if possible, back of valve tag, on zone valve box above valve | This valve allows servicing or modification to the distribution piping or Medical Gas Outlets - CO2. A Zone Valve - Carbon Dioxide is installed upstream of a Service Valve - Carbon Dioxide. This valve is installed on wall in the nurse’s stations to allow for easy access in case of a fire or other emergency. |  | 21-04 20 60 30 | Gas Systems | 22-22 63 00 | Gas Systems for Laboratory and Healthcare Facilities | 23-25 33 29 | Medical Gas Shutoff Valves
Supplemental Elements | D2060.30d.99 | n/a | D2060.30d - Plumbing - Carbon Dioxide Gas - [Supplemental Elements] Carbon Dioxide Gas | D2060.30d - Plumbing - Carbon Dioxide Gas | [Supplemental Elements] Carbon Dioxide Gas |  | D. Plumbing - Carbon Dioxide Gas - [Supplemental Elements] Carbon Dioxide Gas | D. Plumbing - Carbon Dioxide Gas | [Supplemental Elements] Carbon Dioxide Gas |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.40 |  | D2060.40 - Plumbing - Chemical-Waste Systems | D2060.40 - Plumbing - Chemical-Waste Systems |  |  | D. Plumbing - Chemical-Waste Systems | D. Plumbing - Chemical-Waste Systems | [5 empty] | General Category |  | 21-04 20 60 40 | Chemical-Waste Systems | 22-22 66 00
System | D2060.40 | Not on One-Line | D2060.40 - Plumbing - Chemical-Waste Systems - (System) Chemical Waste | D2060.40 - Plumbing - Chemical-Waste Systems | (System) Chemical Waste |  | D. Plumbing - Chemical-Waste Systems - (System) Chemical Waste | D. Plumbing - Chemical-Waste Systems | (System) Chemical Waste |  | SYS Chemical Waste ([Area Served]) | Each major component | On control panel | Vessels that were manufactured to accept and store acid waste. |  | 21-04 20 60 90 | Process Support Plumbing System Supplementary Components | 22-40 25 13 | Liquid Acids Piping | 23-39 41 00 | Water and Wastewater Advanced Treatment Equipment
Asset | D2060.40 | Not on One-Line | D2060.40 - Plumbing - Chemical-Waste Systems - Chemical Tank | D2060.40 - Plumbing - Chemical-Waste Systems | Chemical Tank |  | D. Plumbing - Chemical-Waste Systems - Chemical Tank | D. Plumbing - Chemical-Waste Systems | Chemical Tank |  | Chemical Tank | Each Tank | On control panel | Vessel of multiple sizes and configurations generally used for holding various water or other fluid treatment chemical systems. |  | 21-04 20 60 90 | Process Support Plumbing System Supplementary Components | 22-22 66 83 | Chemical-Waste Tanks | 23-27 29 15 | Specialized Tanks
Supplemental Elements | D2060.40.99 | n/a | D2060.40 - Plumbing - Chemical-Waste Systems - [Supplemental Elements] Chemical Waste | D2060.40 - Plumbing - Chemical-Waste Systems | [Supplemental Elements] Chemical Waste |  | D. Plumbing - Chemical-Waste Systems - [Supplemental Elements] Chemical Waste | D. Plumbing - Chemical-Waste Systems | [Supplemental Elements] Chemical Waste |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.50 |  | D2060.50 - Plumbing - Processed Water | D2060.50 - Plumbing - Processed Water |  |  | D. Plumbing - Processed Water | D. Plumbing - Processed Water | [5 empty] | General Category |  | 21-04 20 60 40 | Chemical-Waste Systems | 22-22 66 00
System | D2060.50 | Not on One-Line | D2060.50 - Plumbing - Processed Water - (System) Water Purification - Deionized Water (DI) | D2060.50 - Plumbing - Processed Water | (System) Water Purification - Deionized Water (DI) |  | D. Plumbing - Processed Water - (System) Water Purification - Deionized Water (DI) | D. Plumbing - Processed Water | (System) Water Purification - Deionized Water (DI) |  | SYS Deionized Water (DI) ([Area Served]) | Each filter; pump may be sub-asset | On unit (other than replaceable parts) | A system that removes ions such as calcium, sodium, chlorides from water. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
System | D2060.50 | Not on One-Line | D2060.50 - Plumbing - Processed Water - (System) Water Purification - Reverse Osmosis (RO) | D2060.50 - Plumbing - Processed Water | (System) Water Purification - Reverse Osmosis (RO) |  | D. Plumbing - Processed Water - (System) Water Purification - Reverse Osmosis (RO) | D. Plumbing - Processed Water | (System) Water Purification - Reverse Osmosis (RO) |  | SYS Reverse Osmosis (RO) ([Area Served]) | Each unit | On unit (other than replaceable parts) | Reverse Osmosis is a process in which solids (such as salts) are removed from a solution (=water). This is accomplished by household water pressure pushing the water through a semipermeable membrane. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 16 | Reverse-Osmosis Water Equipment | 23-27 55 29 19 | Reverse Osmosis Units
Supplemental Elements | D2060.50.99 | n/a | D2060.50 - Plumbing - Processed Water - [Supplemental Elements] Water Purification | D2060.50 - Plumbing - Processed Water | [Supplemental Elements] Water Purification |  | D. Plumbing - Processed Water - [Supplemental Elements] Water Purification | D. Plumbing - Processed Water | [Supplemental Elements] Water Purification |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D2060.90 |  | D2060.90 - Plumbing - Heat Trace System | D2060.90 - Plumbing - Heat Trace System |  |  | D. Plumbing - Heat Trace System | D. Plumbing - Heat Trace System | [5 empty] | General Category
System | D2060.90 | Not on One-Line | D2060.90 - Plumbing - Heat Trace System - (System) Heat Trace | D2060.90 - Plumbing - Heat Trace System | (System) Heat Trace |  | D. Plumbing - Heat Trace System - (System) Heat Trace | D. Plumbing - Heat Trace System | (System) Heat Trace |  | SYS Heat Trace ([Area Served]) | Each system | On control panel | Electric heat tracing, heat tape or surface heating, is a system used to maintain or raise the temperature of pipes and vessels. Trace heating takes the form of an electrical heating element run in physical contact along the length of a pipe. The pipe is usually covered with thermal insulation to retain heat losses from the pipe. |  | 21-04 20 30 90 | Building Support Plumbing System Supplementary Components | 22-22 05 33 | Heat Tracing for Plumbing Piping | 23-33 15 15 21 | Pipe Heat Tracing
Supplemental Elements | D2060.90.99 | n/a | D2060.90 - Plumbing - Heat Trace System - [Supplemental Elements] Heat Trace | D2060.90 - Plumbing - Heat Trace System | [Supplemental Elements] Heat Trace |  | D. Plumbing - Heat Trace System - [Supplemental Elements] Heat Trace | D. Plumbing - Heat Trace System | [Supplemental Elements] Heat Trace |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3020.10 |  | D3020.10 - HVAC - Central Heating | D3020.10 - HVAC - Central Heating |  |  | D. HVAC - Central Heating | D. HVAC - Central Heating | [5 empty] | General Category |  | 21-04 30 20 | Heating Systems
System | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - (System) Central Heating | D3020.10 - HVAC - Central Heating | (System) Central Heating |  | D. HVAC - Central Heating - (System) Central Heating | D. HVAC - Central Heating | (System) Central Heating |  | SYS Central Heating ([Area Served]) | Each system | No barcode - Track by location | Generic representation of system |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Blowdown Heat Recovery | D3020.10 - HVAC - Central Heating | Blowdown Heat Recovery |  | D. HVAC - Central Heating - Blowdown Heat Recovery | D. HVAC - Central Heating | Blowdown Heat Recovery |  | Blowdown Heat Recovery | Each unit (unless it part of boiler) | On unit | Vessel that receives and separates blowdown stream into flash steam, water and solids. |  | 21-04 30 20 10 | Heat Generation | 22-23 52 83 | Boiler Blowdown Systems
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Blowdown Tank/Separator | D3020.10 - HVAC - Central Heating | Blowdown Tank/Separator |  | D. HVAC - Central Heating - Blowdown Tank/Separator | D. HVAC - Central Heating | Blowdown Tank/Separator |  | Blowdown Tank/Separator | Each Tank | On unit | Vessel receiving boiler blowdown. |  | 21-04 30 20 10 | Heat Generation | 22-23 52 83 | Boiler Blowdown Systems | 23-27 29 19 | Tanks
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Boiler | D3020.10 - HVAC - Central Heating | Boiler |  | D. HVAC - Central Heating - Boiler | D. HVAC - Central Heating | Boiler |  | Boiler | Each Boiler | On control panel, if no control panel on clean space next to boiler "name" | Generates hot water and steam. Variety of designs and sizes, mainly gas and/or fuel fired (reportedly there are electric boilers at TAH). |  | 21-04 30 20 10 | Heat Generation | 22-23 52 00 | Heating Boilers | 23-33 11 00 | Commercial Boilers
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Boiler - Dual Fuel | D3020.10 - HVAC - Central Heating | Boiler | Dual Fuel | D. HVAC - Central Heating - Boiler - Dual Fuel | D. HVAC - Central Heating | Boiler | Dual Fuel | Boiler - Dual Fuel | Each Boiler | On control panel, if no control panel on clean space next to boiler "name" | A boiler is a device that burns gas, oil, electricity, or coal in order to provide steam or hot water to a facility. This type of boiler has a duel fuel capability to burn either oil or natural gas. |  | 21-04 30 20 10 | Heat Generation | 22-23 52 00 | Heating Boilers | 23-33 11 00 | Commercial Boilers
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Boiler - Electric | D3020.10 - HVAC - Central Heating | Boiler | Electric | D. HVAC - Central Heating - Boiler - Electric | D. HVAC - Central Heating | Boiler | Electric | Boiler - Electric | Each Boiler | On control panel, if no control panel on clean space next to boiler "name" | A boiler is a device that burns gas, oil, electricity, or coal in order to provide steam or hot water to a facility. This type of boiler uses electric heating coils as its energy source. |  | 21-04 30 20 10 | Heat Generation | 22-23 52 00 | Heating Boilers | 23-33 11 22 | Electric Boilers
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Boiler - Gas | D3020.10 - HVAC - Central Heating | Boiler | Gas | D. HVAC - Central Heating - Boiler - Gas | D. HVAC - Central Heating | Boiler | Gas | Boiler - Gas | Each Boiler | On control panel, if no control panel on clean space next to boiler "name" | A boiler is a device that burns gas, oil, electricity, or coal in order to provide steam or hot water to a facility. This type of boiler uses gas (natural gas or propane) as its energy source. |  | 21-04 30 20 10 | Heat Generation | 22-23 52 00 | Heating Boilers | 23-33 11 00 | Commercial Boilers
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Boiler - Oil | D3020.10 - HVAC - Central Heating | Boiler | Oil | D. HVAC - Central Heating - Boiler - Oil | D. HVAC - Central Heating | Boiler | Oil | Boiler - Oil | Each Boiler | On control panel, if no control panel on clean space next to boiler "name" | A boiler is a device that burns gas, oil, electricity, or coal in order to provide steam or hot water to a facility. This type of boiler uses oil as its energy source. |  | 21-04 30 20 10 | Heat Generation | 22-23 52 00 | Heating Boilers | 23-33 11 00 | Commercial Boilers
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Boiler Feed Pump | D3020.10 - HVAC - Central Heating | Boiler Feed Pump |  | D. HVAC - Central Heating - Boiler Feed Pump | D. HVAC - Central Heating | Boiler Feed Pump |  | Boiler Feed Pump | Each Pump | On control panel (or pump if no panel) | This is a pump that supplies water to steam boiler(s) whenever the water level falls below a setpoint. |  | 21-04 30 20 10 | Heat Generation | 22-23 53 13 | Boiler Feedwater Pumps | 23-27 17 00 | Pumps
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Deaerator | D3020.10 - HVAC - Central Heating | Deaerator |  | D. HVAC - Central Heating - Deaerator | D. HVAC - Central Heating | Deaerator |  | Deaerator | Each Deaerator | Place barcode on control panel | This is a vessel associated with a boiler system used as a suction head tank for boiler feed pumps and a first stage feedwater heater that scavenges oxygen from condensate and makeup water. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 53 16 | Deaerators
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Deaerator Storage Tank | D3020.10 - HVAC - Central Heating | Deaerator Storage Tank |  | D. HVAC - Central Heating - Deaerator Storage Tank | D. HVAC - Central Heating | Deaerator Storage Tank |  | Deaerator Storage Tank | Each Tank | On vessel | The lower section of a deaerator used to store the feedwater. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 53 16 | Deaerators | 23-27 29 19 | Tanks
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Economizer | D3020.10 - HVAC - Central Heating | Economizer |  | D. HVAC - Central Heating - Economizer | D. HVAC - Central Heating | Economizer |  | Economizer | Each economizer | Place barcode metal and hang from economizer | Vessel to capture the waste heat from boiler stack gases (flue gas) and transfer it to the boiler feedwater. Typically tracked as part of the boiler. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-46 78 47 | Waste Heat Recovery Boilers | 23-27 23 11 | Heat Exchanger Economizers
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Forced Draft Fan | D3020.10 - HVAC - Central Heating | Forced Draft Fan |  | D. HVAC - Central Heating - Forced Draft Fan | D. HVAC - Central Heating | Forced Draft Fan |  | Forced Draft Fan | Each unit | On control panel | Fans supplying combustion air for boiler draft (typically tracked part of the Boiler). |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 65 13 | Forced-Draft Cooling Towers | 23-33 11 23 23 | Boiler Draft Fans
Asset | D3020.10 | Not on One-Line | D3020.10 - HVAC - Central Heating - Furnace | D3020.10 - HVAC - Central Heating | Furnace |  | D. HVAC - Central Heating - Furnace | D. HVAC - Central Heating | Furnace |  | Furnace | Each Furnace | On control panel | Generates heated air (as opposed to a boiler that produces hot water and steam). |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 54 00 | Furnaces | 23-33 13 00 | Furnaces
Asset | D3020.10 | Not on One-Line | D3020.10 - HVAC - Central Heating - Furnace - Electric | D3020.10 - HVAC - Central Heating | Furnace | Electric | D. HVAC - Central Heating - Furnace - Electric | D. HVAC - Central Heating | Furnace | Electric | Furnace - Electric | Each Furnace | On control panel | An enclosed structure that contains a fan/blower and an electric resistance coil to heat the supply air. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 54 13 | Electric-Resistance Furnaces | 23-33 13 15 | Electric Resistance Furnaces
Asset | D3020.10 | Not on One-Line | D3020.10 - HVAC - Central Heating - Furnace - Gas | D3020.10 - HVAC - Central Heating | Furnace | Gas | D. HVAC - Central Heating - Furnace - Gas | D. HVAC - Central Heating | Furnace | Gas | Furnace - Gas | Each Furnace | On control panel | An enclosed structure that contains a fan/blower with a gas fired heat exchanger to heat the supply air. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 54 16 13 | Gas-Fired Furnaces | 23-33 13 19 | Gasoline Fired Furnaces
Asset | D3020.10 | Not on One-Line | D3020.10 - HVAC - Central Heating - Furnace - Oil | D3020.10 - HVAC - Central Heating | Furnace | Oil | D. HVAC - Central Heating - Furnace - Oil | D. HVAC - Central Heating | Furnace | Oil | Furnace - Oil | Each Furnace | On control panel | An enclosed structure that contains a fan/blower and a oil fired heat exchanger to heat the supply air. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 54 16 16 | Oil-Fired Furnaces | 23-33 13 23 | Oil Fired Furnaces
Asset | D3020.10 | D30-1 | D3020.10 - HVAC - Central Heating - Hot Water Heat Exchanger | D3020.10 - HVAC - Central Heating | Hot Water Heat Exchanger |  | D. HVAC - Central Heating - Hot Water Heat Exchanger | D. HVAC - Central Heating | Hot Water Heat Exchanger |  | Hot Water Heat Exchanger | Each unit (unless it part of boiler) | On control panel | A shell and tube or plate type unit for transfer of heat from steam or hot water to water used for comfort heating. The two fluids do not mix. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 57 00 | Heat Exchangers for HVAC | 23-27 23 25 | Fluid Heat Exchangers
Supplemental Elements | D3020.10.99 | n/a | D3020.10 - HVAC - Central Heating - [Supplemental Elements] Central Heating | D3020.10 - HVAC - Central Heating | [Supplemental Elements] Central Heating |  | D. HVAC - Central Heating - [Supplemental Elements] Central Heating | D. HVAC - Central Heating | [Supplemental Elements] Central Heating |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3020.70 |  | D3020.70 - HVAC - Decentralized Heating | D3020.70 - HVAC - Decentralized Heating |  |  | D. HVAC - Decentralized Heating | D. HVAC - Decentralized Heating | [5 empty] | General Category |  | 21-04 30 20 70 | Decentralized Heating Equipment | 22-23 80 00 | Decentralized HVAC Equipment | 23-33 15 00 | HVAC Heating Units
System | D3020.70 | Not on One-Line | D3020.70 - HVAC - Decentralized Heating - (System) Decentralized Heating | D3020.70 - HVAC - Decentralized Heating | (System) Decentralized Heating |  | D. HVAC - Decentralized Heating - (System) Decentralized Heating | D. HVAC - Decentralized Heating | (System) Decentralized Heating |  | SYS Decentralized Heating ([Area Served]) | All units in a defined area | No barcode - Track by location | Generic representation of all distributed decentralized heating units. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D3020.70 | D30-5 | D3020.70 - HVAC - Decentralized Heating - Fan Coil Unit | D3020.70 - HVAC - Decentralized Heating | Fan Coil Unit |  | D. HVAC - Decentralized Heating - Fan Coil Unit | D. HVAC - Decentralized Heating | Fan Coil Unit |  | Fan Coil Unit | Each unit | On operating panel | A fan coil unit is a device that uses a coil and a fan to heat or cool a room typically without connecting to ductwork. Indoor air moves over the coil, which heats or cools the air before pushing it back out into the room. These are essentially smaller and simpler versions of AHU's; usually designed to serve a defined space and fitted with limited or no ducting. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 82 19 | Fan Coil Units | 23-33 33 11 | Fan Coil Units
Asset | D3020.70 | Not on One-Line | D3020.70 - HVAC - Decentralized Heating - Portable Heating Unit | D3020.70 - HVAC - Decentralized Heating | Portable Heating Unit |  | D. HVAC - Decentralized Heating - Portable Heating Unit | D. HVAC - Decentralized Heating | Portable Heating Unit |  | Portable Heating Unit | Each unit | On control panel | Any mobile unit that heats the ambient air. Can be oil, gas or electric fired. Combustion units are direct vent to space. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 80 00 | Decentralized HVAC Equipment | 23-33 15 00 | HVAC Heating Units
Asset | D3020.70 | Not on One-Line | D3020.70 - HVAC - Decentralized Heating - Unit Heater | D3020.70 - HVAC - Decentralized Heating | Unit Heater |  | D. HVAC - Decentralized Heating - Unit Heater | D. HVAC - Decentralized Heating | Unit Heater |  | Unit Heater | Each unit | On control panel | Heater consisting of a fan/blower and an indirect heat exchanger enclosed in a common casing and designed to circulate and warm the air of a continuous enclosed space. Normally used to heat loading docks or mechanical equipment rooms. Can be used to provide freeze protection for large Air Handling Units. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 82 39 | Unit Heaters | 23-33 15 00 | HVAC Heating Units
Asset | D3020.70 | Not on One-Line | D3020.70 - HVAC - Decentralized Heating - Unit Heater - Electric | D3020.70 - HVAC - Decentralized Heating | Unit Heater | Electric | D. HVAC - Decentralized Heating - Unit Heater - Electric | D. HVAC - Decentralized Heating | Unit Heater | Electric | Unit Heater - Electric | Each unit | On control panel | Heater consisting of a fan/blower and an indirect electric heating coil enclosed in a common casing and designed to circulate and warm the air of a continuous enclosed space. Normally used to heat loading docks or mechanical equipment rooms. Can be used to provide freeze protection for large Air Handling Units. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 82 39 | Unit Heaters | 23-33 15 25 17 | Electric HVAC Resistive Unit Heaters
Asset | D3020.70 | Not on One-Line | D3020.70 - HVAC - Decentralized Heating - Unit Heater - Gas | D3020.70 - HVAC - Decentralized Heating | Unit Heater | Gas | D. HVAC - Decentralized Heating - Unit Heater - Gas | D. HVAC - Decentralized Heating | Unit Heater | Gas | Unit Heater - Gas | Each unit | On control panel | Heater consisting of a fan/blower and gas fire furnace indirect heat exchanger enclosed in a common casing and designed to circulate and warm the air of a continuous enclosed space. Normally used to heat loading docks or mechanical equipment rooms. Can be used to provide freeze protection for large Air Handling Units. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 82 39 | Unit Heaters | 23-33 15 19 15 | Forced Air Fuel Fired HVAC Unit Heaters
Asset | D3020.70 | Not on One-Line | D3020.70 - HVAC - Decentralized Heating - Unit Heater - Hot Water | D3020.70 - HVAC - Decentralized Heating | Unit Heater | Hot Water | D. HVAC - Decentralized Heating - Unit Heater - Hot Water | D. HVAC - Decentralized Heating | Unit Heater | Hot Water | Unit Heater - Hot Water | Each unit | On control panel | Heater consisting of a fan/blower and an indirect hot water heat exchanger enclosed in a common casing and designed to circulate and warm the air of a continuous enclosed space. Normally used to heat loading docks or mechanical equipment rooms. Can be used to provide freeze protection for large Air Handling Units. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 82 39 | Unit Heaters | 23-33 15 21 | Hydronic HVAC Heaters
Asset | D3020.70 | Not on One-Line | D3020.70 - HVAC - Decentralized Heating - Unit Heater - Steam | D3020.70 - HVAC - Decentralized Heating | Unit Heater | Steam | D. HVAC - Decentralized Heating - Unit Heater - Steam | D. HVAC - Decentralized Heating | Unit Heater | Steam | Unit Heater - Steam | Each unit | On operating panel, if no panel on side of the unit housing | Heater consisting of a fan/blower and an indirect steam heat exchanger enclosed in a common casing and designed to circulate and warm the air of a continuous enclosed space. Normally used to heat loading docks or mechanical equipment rooms. Can be used to provide freeze protection for large Air Handling Units. |  | 21-04 30 20 90 | Heating System Supplementary Components | 22-23 82 39 | Unit Heaters | 23-33 15 29 | HVAC Steam Hot Water Converters
Supplemental Elements | D3020.70.99 | n/a | D3020.70 - HVAC - Decentralized Heating - [Supplemental Elements] Decentralized Heating | D3020.70 - HVAC - Decentralized Heating | [Supplemental Elements] Decentralized Heating |  | D. HVAC - Decentralized Heating - [Supplemental Elements] Decentralized Heating | D. HVAC - Decentralized Heating | [Supplemental Elements] Decentralized Heating |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3030.10 |  | D3030.10 - HVAC - Central Cooling | D3030.10 - HVAC - Central Cooling |  |  | D. HVAC - Central Cooling | D. HVAC - Central Cooling | [5 empty] | General Category |  | 21-04 30 30 | Cooling Systems | 22-23 60 00 | Central Cooling Equipment
System | D3030.10 | D30-2 | D3030.10 - HVAC - Central Cooling - (System) Central Cooling | D3030.10 - HVAC - Central Cooling | (System) Central Cooling |  | D. HVAC - Central Cooling - (System) Central Cooling | D. HVAC - Central Cooling | (System) Central Cooling |  | SYS Central Cooling ([Area Served]) | Each system | No barcode - Track by location | Generic representation of system. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D3030.10 | D30-2 | D3030.10 - HVAC - Central Cooling - Chilled Water Heat Exchanger | D3030.10 - HVAC - Central Cooling | Chilled Water Heat Exchanger |  | D. HVAC - Central Cooling - Chilled Water Heat Exchanger | D. HVAC - Central Cooling | Chilled Water Heat Exchanger |  | Chilled Water Heat Exchanger | Each HX | On control panel | Water-to-water non-contact heat exchangers utilized in chilled water distribution systems. Can be of multiple designs; typically shell and tube or plate and frame design in chilled water applications. |  | 21-04 30 30 10 | Central Cooling | 22-23 57 00 | Heat Exchangers for HVAC | 23-27 23 00 | Heat Exchangers
Asset | D3030.10 | D30-2 | D3030.10 - HVAC - Central Cooling - Chiller - Air Cooled | D3030.10 - HVAC - Central Cooling | Chiller | Air Cooled | D. HVAC - Central Cooling - Chiller - Air Cooled | D. HVAC - Central Cooling | Chiller | Air Cooled | Chiller - Air Cooled | Each unit | On control panel | Typically a larger tonnage central refrigeration machine rejecting heat directly to the exterior and connected to a CHW loop that feeds HVAC equipment for space cooling. |  | 21-04 30 30 10 | Central Cooling | 22-23 64 00 | Packaged Water Chillers | 23-33 21 13 | Chillers
Asset | D3030.10 | D30-2 | D3030.10 - HVAC - Central Cooling - Chiller - Type to be determined | D3030.10 - HVAC - Central Cooling | Chiller | Type to be determined | D. HVAC - Central Cooling - Chiller - Type to be determined | D. HVAC - Central Cooling | Chiller | Type to be determined | Chiller - [Air or Water Cooled] | Each unit | On control panel | Needs to be classified either as air cooled or water cooled chiller. |  | 21-04 30 30 10 | Central Cooling | 22-23 64 00 | Packaged Water Chillers | 23-33 21 13 | Chillers
Asset | D3030.10 | D30-2 | D3030.10 - HVAC - Central Cooling - Chiller - Water Cooled | D3030.10 - HVAC - Central Cooling | Chiller | Water Cooled | D. HVAC - Central Cooling - Chiller - Water Cooled | D. HVAC - Central Cooling | Chiller | Water Cooled | Chiller - Water Cooled | Each unit | On control panel | Typically a larger tonnage central refrigeration machine rejecting heat to a water circuit and connected to a CHW loop that feeds HVAC equipment for space cooling. |  | 21-04 30 30 10 | Central Cooling | 22-23 64 00 | Packaged Water Chillers | 23-33 21 13 | Chillers
Asset | D3030.10 | D30-2 | D3030.10 - HVAC - Central Cooling - Cooling Tower | D3030.10 - HVAC - Central Cooling | Cooling Tower |  | D. HVAC - Central Cooling - Cooling Tower | D. HVAC - Central Cooling | Cooling Tower |  | Cooling Tower | Each tower | On control panel, if no panel on dunnage under tower | Typically, roof-mounted structures that reject heat from condensing water used to cool the condenser section of larger central chillers. Associated with water-cooled chilling capacity only. |  | 21-04 30 30 50 | Thermal Cooling Storage | 22-23 65 00 | Cooling Towers | 23-33 23 00 | Cooling Towers
Asset | D3030.10 | D30-2 | D3030.10 - HVAC - Central Cooling - Cooling Tower Pump | D3030.10 - HVAC - Central Cooling | Cooling Tower Pump |  | D. HVAC - Central Cooling - Cooling Tower Pump | D. HVAC - Central Cooling | Cooling Tower Pump |  | Cooling Tower Pump | Each pump (set) | On pump or skid | A pump of high volume and low delta P for circulating cooling water from equipment such as a chiller to a outdoor heat rejection unit. Typically part of an open loop but can be a closed loop. |  | 21-04 30 30 50 | Thermal Cooling Storage | 22-42 21 00 | Process Cooling Towers | 23-27 17 00 | Pumps
Asset | D3030.10 | D30-2 | D3030.10 - HVAC - Central Cooling - Pump Out Receiver Tank | D3030.10 - HVAC - Central Cooling | Pump Out Receiver Tank |  | D. HVAC - Central Cooling - Pump Out Receiver Tank | D. HVAC - Central Cooling | Pump Out Receiver Tank |  | Pump Out Receiver Tank | Each pump receiver tank | On unit | Tank for receiving refrigerant when performing chilling system maintenance. |  | 21-04 30 30 | Cooling Systems | 22-23 21 23 | Hydronic Pumps | 23-27 29 19 | Tanks
Supplemental Elements | D3030.10.99 | n/a | D3030.10 - HVAC - Central Cooling - [Supplemental Elements] Central Cooling | D3030.10 - HVAC - Central Cooling | [Supplemental Elements] Central Cooling |  | D. HVAC - Central Cooling - [Supplemental Elements] Central Cooling | D. HVAC - Central Cooling | [Supplemental Elements] Central Cooling |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3030.70 |  | D3030.70 - HVAC - Decentralized Cooling | D3030.70 - HVAC - Decentralized Cooling |  |  | D. HVAC - Decentralized Cooling | D. HVAC - Decentralized Cooling | [5 empty] | General Category |  | 21-04 30 30 70 | Decentralized Cooling | 22-23 80 00 | Decentralized HVAC Equipment
System | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - (System) Decentralized Cooling | D3030.70 - HVAC - Decentralized Cooling | (System) Decentralized Cooling |  | D. HVAC - Decentralized Cooling - (System) Decentralized Cooling | D. HVAC - Decentralized Cooling | (System) Decentralized Cooling |  | SYS Decentralized Cooling ([Area Served]) | All units in a defined area | No barcode - Track by location | Generic representation of all distributed decentralized cooling units, larger than mini-splits. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
System | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - (System) Split Type | D3030.70 - HVAC - Decentralized Cooling | (System) Split Type |  | D. HVAC - Decentralized Cooling - (System) Split Type | D. HVAC - Decentralized Cooling | (System) Split Type |  | SYS Split System ([Area Served]) | All units in a defined area | No barcode - Track by location | Generic representation of all distributed Mini-split systems. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Air Conditioning Unit (DX Cooling) | D3030.70 - HVAC - Decentralized Cooling | Air Conditioning Unit (DX Cooling) |  | D. HVAC - Decentralized Cooling - Air Conditioning Unit (DX Cooling) | D. HVAC - Decentralized Cooling | Air Conditioning Unit (DX Cooling) |  | Air Conditioning Unit (DX Cooling) | Each unit | On control panel | A direct expansion air conditioning (DX) system using refrigerant to directly cool the supply air to an occupied space. May reject heat directly to exterior air or to a water loop. Typically a commercial grade unit in tonnages over what would be considered a split-type unit. |  | 21-04 30 30 90 | Cooling System Supplementary Components | 22-23 73 23 | Custom Indoor Central-Station Air-Handling Units | 23-33 39 11 | Air Conditioners
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Computer Room Air Conditioning Unit | D3030.70 - HVAC - Decentralized Cooling | Computer Room Air Conditioning Unit |  | D. HVAC - Decentralized Cooling - Computer Room Air Conditioning Unit | D. HVAC - Decentralized Cooling | Computer Room Air Conditioning Unit |  | Computer Room Air Conditioning Unit | Each system | Track by inside and outside location | Used to monitor and maintain the temperature of room in which the computing equipment operates. They maintain the proper air distribution and humidity of the network room. CRACs are most commonly used in data centers. |  | 21-04 30 30 90 | Cooling System Supplementary Components | 22-23 81 23 | Computer-Room Air-Conditioners | 23-33 45 00 | HVAC Coolers
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Computer Room Air Conditioning Unit - Condenser | D3030.70 - HVAC - Decentralized Cooling | Computer Room Air Conditioning Unit | Condenser | D. HVAC - Decentralized Cooling - Computer Room Air Conditioning Unit - Condenser | D. HVAC - Decentralized Cooling | Computer Room Air Conditioning Unit | Condenser | Computer Room Air Conditioning Unit - Condenser ([Units served]) | Each unit | On control panel | A computer room air conditioning (CRAC) unit is a device that monitors and maintains the temperature, air distribution and humidity in a network room or data center. CRAC units are replacing air-conditioning units that were used in the past to cool data centers. This is the condenser potion of that system. |  | 21-04 30 30 90 | Cooling System Supplementary Components | 22-42 23 13 | Process Condensers | 23-33 43 00 | HVAC Condenser Units
Asset | D3030.70 | D30-3 | D3030.70 - HVAC - Decentralized Cooling - Dry Cooler (DX) | D3030.70 - HVAC - Decentralized Cooling | Dry Cooler (DX) |  | D. HVAC - Decentralized Cooling - Dry Cooler (DX) | D. HVAC - Decentralized Cooling | Dry Cooler (DX) |  | Dry Cooler (DX) ([Unit served]) | Each cooler (unless it is tracked in ACU) | On Unit | A unit consisting of a refrigerant coil and fan. Hot refrigerant from a separate compressor passes through the coil. Ambient air is drawn over the coil absorbing heat from the refrigerant. The refrigerant then moves to the separate evaporator. |  | 21-04 30 30 | Cooling Systems | 22-42 31 23 | Refrigerant Dryers | 23-33 45 11 | HVAC Dry Coolers
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Heat Pump | D3030.70 - HVAC - Decentralized Cooling | Heat Pump |  | D. HVAC - Decentralized Cooling - Heat Pump | D. HVAC - Decentralized Cooling | Heat Pump |  | Heat Pump ([Unit Served]) | Each Unit | On Unit | Heat pumps are similar to a DX air conditioning unit. The major difference is that the heat pump can be used either in heating mode or cooling mode, as required. When a heat pump is used for heating, it employs the same basic refrigeration-type cycle used by an air conditioner or a refrigerator, but in the opposite direction – releasing heat into the conditioned space rather than the surrounding environment. In this use, heat pumps generally draw heat from the cooler external air or from the ground. |  | 21-04 30 30 90 | Cooling System Supplementary Components | 22-23 81 43 | Air-Source Unitary Heat Pumps | 23-33 17 00 | Heat Pumps
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Packaged Terminal Air Conditioner (PTAC) | D3030.70 - HVAC - Decentralized Cooling | Packaged Terminal Air Conditioner (PTAC) |  | D. HVAC - Decentralized Cooling - Packaged Terminal Air Conditioner (PTAC) | D. HVAC - Decentralized Cooling | Packaged Terminal Air Conditioner (PTAC) |  | Packaged Terminal Air Conditioner (PTAC) | Each unit | On unit | A self contained heating and/or unit designed typically to serve on modest sized space. Usually mounted through the wall under windows but may be vertical also.. Exterior air is used for condensing. Typically units are mounted in wall sleeves and can be withdrawn for service or replacement.
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Portable Cooling Unit | D3030.70 - HVAC - Decentralized Cooling | Portable Cooling Unit |  | D. HVAC - Decentralized Cooling - Portable Cooling Unit | D. HVAC - Decentralized Cooling | Portable Cooling Unit |  | Portable Cooling Unit | Each unit | On side of the unit housing | Any mobile unit that cools the ambient air. The refrigeration system typically has an air cooled condenser but it may be water cooled. |  | 21-04 30 30 90 | Cooling System Supplementary Components | 22-23 81 16 | Room Air-Conditioners | 23-33 39 19 13 | Portable Packaged Terminal Air Conditioners
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Split Type Air Conditioning Unit (DX) | D3030.70 - HVAC - Decentralized Cooling | Split Type Air Conditioning Unit (DX) |  | D. HVAC - Decentralized Cooling - Split Type Air Conditioning Unit (DX) | D. HVAC - Decentralized Cooling | Split Type Air Conditioning Unit (DX) |  | Split Type Air Conditioning Unit (DX) | Each system | Track by inside and outside location | A split air conditioner consists of an outdoor unit and an indoor unit. Split systems typically have one or more evaporators indoors, generally each under about 36,000 BTU, with a condensing unit typically air cooled and located outdoors. |  | 21-04 30 30 90 | Cooling System Supplementary Components | 22-23 81 26 | Split-System Air-Conditioners | 23-33 39 21 | Split System Air Conditioning Units
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Split Type Air Conditioning Unit (DX) - Condenser | D3030.70 - HVAC - Decentralized Cooling | Split Type Air Conditioning Unit (DX) | Condenser | D. HVAC - Decentralized Cooling - Split Type Air Conditioning Unit (DX) - Condenser | D. HVAC - Decentralized Cooling | Split Type Air Conditioning Unit (DX) | Condenser | Split Type Air Conditioning Unit (DX) - Condenser ([Units served]) | Each unit | On unit | This category is to be used if the outside condenser of a split system is to be tracked separately from the split system. The condensing outdoor unit is installed on or near the exterior wall of the room that is being cooled. This unit houses the compressor and condenser coil. |  | 21-04 30 30 90 | Cooling System Supplementary Components | 22-42 23 13 | Process Condensers | 23-33 43 00 | HVAC Condenser Units
Asset | D3030.70 | Not on One-Line | D3030.70 - HVAC - Decentralized Cooling - Window Air Conditioning Unit | D3030.70 - HVAC - Decentralized Cooling | Window Air Conditioning Unit |  | D. HVAC - Decentralized Cooling - Window Air Conditioning Unit | D. HVAC - Decentralized Cooling | Window Air Conditioning Unit |  | Window Air Conditioning Unit | Generic asset | On Unit Casing (not cover) | This is an air conditioning unit that is mounted in either a window or through a wall. It provides DX cooling. |  | 21-04 30 30 90 | Cooling System Supplementary Components | 22-23 81 16 | Room Air-Conditioners | 23-33 39 19 15 | Window Packaged Terminal Air Conditioners
Supplemental Elements | D3030.70.99 | n/a | D3030.70 - HVAC - Decentralized Cooling - [Supplemental Elements] Decentralized Cooling | D3030.70 - HVAC - Decentralized Cooling | [Supplemental Elements] Decentralized Cooling |  | D. HVAC - Decentralized Cooling - [Supplemental Elements] Decentralized Cooling | D. HVAC - Decentralized Cooling | [Supplemental Elements] Decentralized Cooling |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Supplemental Elements | D3030.70.99 | n/a | D3030.70 - HVAC - Decentralized Cooling - [Supplemental Elements] Split Type | D3030.70 - HVAC - Decentralized Cooling | [Supplemental Elements] Split Type |  | D. HVAC - Decentralized Cooling - [Supplemental Elements] Split Type | D. HVAC - Decentralized Cooling | [Supplemental Elements] Split Type |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3050.10 |  | D3050.10 - HVAC - Hydronic Distribution | D3050.10 - HVAC - Hydronic Distribution |  |  | D. HVAC - Hydronic Distribution | D. HVAC - Hydronic Distribution | [5 empty] | General Category |  | 21-04 30 50 | Facility HVAC Distribution Systems
System | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - (System) Hydronic Distribution | D3050.10 - HVAC - Hydronic Distribution | (System) Hydronic Distribution |  | D. HVAC - Hydronic Distribution - (System) Hydronic Distribution | D. HVAC - Hydronic Distribution | (System) Hydronic Distribution |  | SYS Hydronic Distribution ([Area Served]) | Each system | No barcode - Track by location | Generic representation of system. This is often tracked as part of central heating or central cooling. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Air Separator | D3050.10 - HVAC - Hydronic Distribution | Air Separator |  | D. HVAC - Hydronic Distribution - Air Separator | D. HVAC - Hydronic Distribution | Air Separator |  | Air Separator | Each Unit | On unit | A chamber installed in a hydronic line that diverts flow to remove entrained air that impedes heat transfer, and in some cases removes solid impurities. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 16 | Hydronic Piping Specialties
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Chilled Water Pump | D3050.10 - HVAC - Hydronic Distribution | Chilled Water Pump |  | D. HVAC - Hydronic Distribution - Chilled Water Pump | D. HVAC - Hydronic Distribution | Chilled Water Pump |  | Chilled Water Pump | Each Pump | On control panel | Chilled water pump associated with a chilled water machine/central chilling plant. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 16 | Hydronic Piping Specialties | 23-27 17 00 | Pumps
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Chilled Water Pump - Primary | D3050.10 - HVAC - Hydronic Distribution | Chilled Water Pump | Primary | D. HVAC - Hydronic Distribution - Chilled Water Pump - Primary | D. HVAC - Hydronic Distribution | Chilled Water Pump | Primary | Chilled Water Pump - Primary | Each Pump | On control panel | Chilled water pump associated with a chilled water machine/central chilling plant that supplies water from/to the chiller unit(s). |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 16 | Hydronic Piping Specialties | 23-27 17 00 | Pumps
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Chilled Water Pump - Secondary | D3050.10 - HVAC - Hydronic Distribution | Chilled Water Pump | Secondary | D. HVAC - Hydronic Distribution - Chilled Water Pump - Secondary | D. HVAC - Hydronic Distribution | Chilled Water Pump | Secondary | Chilled Water Pump - Secondary | Each Pump | On control panel | Chilled water pump associated with a central chilling plant having a primary/secondary pumping scheme and which distributes water to the loop/building loads. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 16 | Hydronic Piping Specialties | 23-27 17 00 | Pumps
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Condenser Water Pump | D3050.10 - HVAC - Hydronic Distribution | Condenser Water Pump |  | D. HVAC - Hydronic Distribution - Condenser Water Pump | D. HVAC - Hydronic Distribution | Condenser Water Pump |  | Condenser Water Pump | Each Pump | On control panel | The condenser water pump in plant refrigeration systems circulates condenser water. The condenser water pump circulates return condenser water from the chiller back to the cooling tower. The cooling tower then cools the condenser water, and the condenser water is supplied back to the chiller. Note: Use care with nomenclature; this should include water-cooled chilling system pumps (i.e. tower pumps); this category is easily confused with condensate systems which are associated with steam system return piping |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 16 | Hydronic Piping Specialties | 23-27 17 00 | Pumps
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Expansion Tank | D3050.10 - HVAC - Hydronic Distribution | Expansion Tank |  | D. HVAC - Hydronic Distribution - Expansion Tank | D. HVAC - Hydronic Distribution | Expansion Tank |  | Expansion Tank | Each Tank | On Tank | A tank found in closed loop hydronic systems to alleviate pressure and temperature fluctuations. Note, this is a high-likelihood miscategorization candidate. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 16 | Hydronic Piping Specialties | 23-27 29 19 | Tanks
Asset | D3050.10 | Not on One-Line | D3050.10 - HVAC - Hydronic Distribution - Glycol Pump | D3050.10 - HVAC - Hydronic Distribution | Glycol Pump |  | D. HVAC - Hydronic Distribution - Glycol Pump | D. HVAC - Hydronic Distribution | Glycol Pump |  | Glycol Pump | Each pump | On control panel | Glycol pumps circulate water with an antifreeze to avoid coil freezing and/or achieve lower air discharge temperatures. Often a packaged, air-cooled glycol system is located on a rooftop. Glycol systems can be treated as a package; i.e. call pumps, tank, heat exchanger, etc. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 23 00 | Refrigerant Piping | 23-27 17 00 | Pumps
Asset | D3050.10 | Not on One-Line | D3050.10 - HVAC - Hydronic Distribution - Glycol Tank | D3050.10 - HVAC - Hydronic Distribution | Glycol Tank |  | D. HVAC - Hydronic Distribution - Glycol Tank | D. HVAC - Hydronic Distribution | Glycol Tank |  | Glycol Tank | Each tank | On tank | Reservoir in a closed loop glycol cooling system. We may want to treat glycol systems as a package; i.e. call pumps, tank, HX, etc... all one asset. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 23 16 | Refrigerant Piping Specialties | 23-27 29 19 | Tanks
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Heating Hot Water Pump | D3050.10 - HVAC - Hydronic Distribution | Heating Hot Water Pump |  | D. HVAC - Hydronic Distribution - Heating Hot Water Pump | D. HVAC - Hydronic Distribution | Heating Hot Water Pump |  | Heating Hot Water Pump | Each Pump | On control panel | Pumps of various service configurations that deliver CHW to the distribution system. Category includes larger production - duty pumps (these could be plant vary-prime---usually with an associated VFD---, primary and secondary configs) found in the plant, as well as those that may be distributed out in the chilled water distribution network. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 23 | Hydronic Pumps | 23-27 17 00 | Pumps
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Linear Accelerator Cooling Water Circuit | D3050.10 - HVAC - Hydronic Distribution | Linear Accelerator Cooling Water Circuit |  | D. HVAC - Hydronic Distribution - Linear Accelerator Cooling Water Circuit | D. HVAC - Hydronic Distribution | Linear Accelerator Cooling Water Circuit |  | Linear Accelerator Cooling Water Circuit | To each Machine | Pipe or valve tags on facility supply and return | Facility supply and return water provided to remove heat from the LICAC. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 16 | Hydronic Piping Specialties
Asset | D3050.10 | Not on One-Line | D3050.10 - HVAC - Hydronic Distribution - Make-up Pump | D3050.10 - HVAC - Hydronic Distribution | Make-up Pump |  | D. HVAC - Hydronic Distribution - Make-up Pump | D. HVAC - Hydronic Distribution | Make-up Pump |  | Make-up Pump | Each Pump | On control panel | Pump used to replenish hydronic systems for water loss due to evaporation, leaks, etc. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 23 | Hydronic Pumps | 23-27 17 00 | Pumps
Asset | D3050.10 | Not on One-Line | D3050.10 - HVAC - Hydronic Distribution - Make-up Tank | D3050.10 - HVAC - Hydronic Distribution | Make-up Tank |  | D. HVAC - Hydronic Distribution - Make-up Tank | D. HVAC - Hydronic Distribution | Make-up Tank |  | Make-up Tank | Each Tank | On tank | Storage tank used to replenish hydronic systems for water loss due to evaporation or leaks. Normally associated with a make-up pump that will activate on either low system pressure or level. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 16 | Hydronic Piping Specialties | 23-27 29 19 | Tanks
Asset | D3050.10 | D30-4 | D3050.10 - HVAC - Hydronic Distribution - Reheat Pump | D3050.10 - HVAC - Hydronic Distribution | Reheat Pump |  | D. HVAC - Hydronic Distribution - Reheat Pump | D. HVAC - Hydronic Distribution | Reheat Pump |  | Reheat Pump | Each Pump | On control panel | This category pertains to reheat for final space conditioning requiring humidity control/fine tuning of temp for conditioned air. Distinguish from domestic (potable) hot water; also sometimes confused with HW hydronic system pumps. |  | 21-04 30 50 10 | Facility Hydronic Distribution | 22-23 21 23 | Hydronic Pumps | 23-27 17 00 | Pumps
Supplemental Elements | D3050.10.99 | n/a | D3050.10 - HVAC - Hydronic Distribution - [Supplemental Elements] Hydronic Distribution | D3050.10 - HVAC - Hydronic Distribution | [Supplemental Elements] Hydronic Distribution |  | D. HVAC - Hydronic Distribution - [Supplemental Elements] Hydronic Distribution | D. HVAC - Hydronic Distribution | [Supplemental Elements] Hydronic Distribution |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3050.30 |  | D3050.30 - HVAC - Steam Distribution | D3050.30 - HVAC - Steam Distribution |  |  | D. HVAC - Steam Distribution | D. HVAC - Steam Distribution | [5 empty] | General Category |  | 21-04 30 50 30 | Facility Steam Distribution
System | D3050.30 | D30-1 | D3050.30 - HVAC - Steam Distribution - (System) Steam Distribution | D3050.30 - HVAC - Steam Distribution | (System) Steam Distribution |  | D. HVAC - Steam Distribution - (System) Steam Distribution | D. HVAC - Steam Distribution | (System) Steam Distribution |  | SYS Steam Distribution ([Area Served]) | Each system | No barcode - Track by location | Generic representation of system. This is often tracked as part of central heating. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D3050.30 | D30-1 | D3050.30 - HVAC - Steam Distribution - Condensate Return Pump | D3050.30 - HVAC - Steam Distribution | Condensate Return Pump |  | D. HVAC - Steam Distribution - Condensate Return Pump | D. HVAC - Steam Distribution | Condensate Return Pump |  | Condensate Return Pump | Each Pump or Pump Set (only if standalone, otherwise this is part of Condensate Return Tank) | On control panel | Pumps that return condensate drains from the steam heating system back to the condensate header and to the steam production plant. (Typically tracked as part of the Condensate Return Tank.) |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 22 23 | Steam Condensate Pumps | 23-27 17 00 | Pumps
Asset | D3050.30 | D30-1 | D3050.30 - HVAC - Steam Distribution - Condensate Return Tank | D3050.30 - HVAC - Steam Distribution | Condensate Return Tank |  | D. HVAC - Steam Distribution - Condensate Return Tank | D. HVAC - Steam Distribution | Condensate Return Tank |  | Condensate Return Tank | Each Tank | On control panel | Tanks that receive condensate drains from the steam heating system, which are then pumps back to the condensate header by its associated pump to the steam production plant. Condensate return components are in many but not all cases mounted integrally to a condensate return tank. For condition assessment purposes, WHEN Condensate Pumps, Condensate Return Pumps, Flash Tanks and/or Vacuum Pumps (3050.30.b, e, g, h) are integrally mounted to the Condensate tank, these assets are to be consolidated into a single asset under Condensate Return Tank. In many cases both condensate return and/or vacuum pumps (up to 4 total) will be found on a single tank. |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 22 16 | Steam and Condensate Heating Piping Specialties | 23-27 29 19 | Tanks
Asset | D3050.30 | D30-1 | D3050.30 - HVAC - Steam Distribution - Condensate Vacuum Pump | D3050.30 - HVAC - Steam Distribution | Condensate Vacuum Pump |  | D. HVAC - Steam Distribution - Condensate Vacuum Pump | D. HVAC - Steam Distribution | Condensate Vacuum Pump |  | Condensate Vacuum Pump | Each Unit (only if standalone, otherwise this is part of Condensate Return Tank) | On control panel | Pumps operating at negative pressure that return condensate drains from the steam heating system back to the condensate header and to the steam production plant. (Typically tracked as part of the Condensate Return Tank.) |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 22 00 | Steam and Condensate Piping and Pumps | 23-27 17 00 | Pumps
Asset | D3050.30 | D30-1 | D3050.30 - HVAC - Steam Distribution - Flash Tank | D3050.30 - HVAC - Steam Distribution | Flash Tank |  | D. HVAC - Steam Distribution - Flash Tank | D. HVAC - Steam Distribution | Flash Tank |  | Flash Tank | Each Tank (only if standalone, otherwise this is part of Condensate Return Tank) | On tag chained to tank | Tank that receives vapor from steam distribution system elements and separates and returns steam to system while flashing condensate. |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 22 16 | Steam and Condensate Heating Piping Specialties | 23-27 29 15 13 11 | Steam Flash Tanks
Asset | D3050.30 | D30-1 | D3050.30 - HVAC - Steam Distribution - Steam Pressure Reducing Valve | D3050.30 - HVAC - Steam Distribution | Steam Pressure Reducing Valve |  | D. HVAC - Steam Distribution - Steam Pressure Reducing Valve | D. HVAC - Steam Distribution | Steam Pressure Reducing Valve |  | Steam Pressure Reducing Valve | Each Valve | On tag chained to valve | Valve assembly typically utilizing a pneumatic valve that reduces steam from distribution pressure down to LP (<15psig) for further distribution to end-use equipment. |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 22 16 | Steam and Condensate Heating Piping Specialties | 23-27 31 47 | Pressure Regulating Valves
Asset | D3050.30 | Not on One-Line | D3050.30 - HVAC - Steam Distribution - Steam Surface Condenser Hotwell Condensate Pump | D3050.30 - HVAC - Steam Distribution | Steam Surface Condenser Hotwell Condensate Pump |  | D. HVAC - Steam Distribution - Steam Surface Condenser Hotwell Condensate Pump | D. HVAC - Steam Distribution | Steam Surface Condenser Hotwell Condensate Pump |  | Steam Surface Condenser Hotwell Condensate Pump | Each Pump | On control panel | Pump associated with a surface condenser that collects and returns condensate accumulation from the hotwell (lowest point) of the condenser to the boiler feedwater system. |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 22 00 | Steam and Condensate Piping and Pumps | 23-27 17 00 | Pumps
Asset | D3050.30 | Not on One-Line | D3050.30 - HVAC - Steam Distribution - Steam Surface Condenser Hotwell Vacuum Pump | D3050.30 - HVAC - Steam Distribution | Steam Surface Condenser Hotwell Vacuum Pump |  | D. HVAC - Steam Distribution - Steam Surface Condenser Hotwell Vacuum Pump | D. HVAC - Steam Distribution | Steam Surface Condenser Hotwell Vacuum Pump |  | Steam Surface Condenser Hotwell Vacuum Pump | Each Pump | On control panel (rotating pump); On nozzle body (ejector) | Pump associated with a surface condenser that is designed to pull vacuum on the condenser vessel. Note: These can also be ejector devices which perform an identical function but do not have rotating elements. Classify these in this category also. |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 22 00 | Steam and Condensate Piping and Pumps | 23-27 17 00 | Pumps
Asset | D3050.30 | D30-1 | D3050.30 - HVAC - Steam Distribution - Steam Trap | D3050.30 - HVAC - Steam Distribution | Steam Trap |  | D. HVAC - Steam Distribution - Steam Trap | D. HVAC - Steam Distribution | Steam Trap |  | Steam Trap | One placeholder per campus, pointing to vendor-performed PM | On tag chained to trap | A steam trap is a device used to discharge condensates and non-condensable gases with a negligible consumption or loss of live steam. Most steam traps are nothing more than automatic valves. They open, close or modulate automatically. |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 22 16 | Steam and Condensate Heating Piping Specialties | 23-27 37 15 | Steam Traps
Supplemental Elements | D3050.30.99 | n/a | D3050.30 - HVAC - Steam Distribution - [Supplemental Elements] Steam Distribution | D3050.30 - HVAC - Steam Distribution | [Supplemental Elements] Steam Distribution |  | D. HVAC - Steam Distribution - [Supplemental Elements] Steam Distribution | D. HVAC - Steam Distribution | [Supplemental Elements] Steam Distribution |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3050.50 |  | D3050.50 - HVAC - Air Distribution | D3050.50 - HVAC - Air Distribution |  |  | D. HVAC - Air Handling | D. HVAC - Air Handling | [5 empty] | General Category |  | 21-04 30 50 50 | HVAC Air Distribution
System | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - (System) Air Distribution | D3050.50 - HVAC - Air Distribution | (System) Air Distribution |  | D. HVAC - Air Handling - (System) Air Distribution | D. HVAC - Air Handling | (System) Air Distribution |  | SYS Air Distribution ([Area Served]) | Each system | No barcode - Track by location | Generic representation of system. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D3050.50 | Not on One-Line | D3050.50 - HVAC - Air Distribution - Air Curtain | D3050.50 - HVAC - Air Distribution | Air Curtain |  | D. HVAC - Air Handling - Air Curtain | D. HVAC - Air Handling | Air Curtain |  | Air Curtain | Each Air Curtain | Barcode placed on On/Off switch | Device that forces a stream of air down through a doorway to separate spaces and reduce contamination/air mixing between spaces |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 34 33 | Air Curtains | 23-33 31 11 | Air Curtains
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Air Handling Unit | D3050.50 - HVAC - Air Distribution | Air Handling Unit |  | D. HVAC - Air Handling - Air Handling Unit | D. HVAC - Air Handling | Air Handling Unit |  | AHU ([Area Served]) | Air Handler is tracked as asset; other components are tracked in Sub Assets | On outside, visible for typical approach | Device used to regulate and circulate air as part of a heating, ventilating, and air-conditioning (HVAC) system. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 73 00 | Indoor Central-Station Air-Handling Units | 23-33 25 00 | Air Handling Units
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Air Handling Unit - Heat Recovery Unit | D3050.50 - HVAC - Air Distribution | Air Handling Unit | Heat Recovery Unit | D. HVAC - Air Handling - Air Handling Unit - Heat Recovery Unit | D. HVAC - Air Handling | Air Handling Unit | Heat Recovery Unit | AHU - Heat Recovery Unit ([Area Served]) | Each unit | On housing or panel | An air handler that transfers energy from the air exhausting the building to the air being conditioned and supplied to the building. Transfer device may be a glycol loop, energy wheel or fixed heat exchanger. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-46 78 49 | Waste Heat Recovery Heat Exchangers | 23-39 43 17 23 | Waste Heat Recovery Heat Exchangers
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Air Handling Unit - Indoor Unit | D3050.50 - HVAC - Air Distribution | Air Handling Unit | Indoor Unit | D. HVAC - Air Handling - Air Handling Unit - Indoor Unit | D. HVAC - Air Handling | Air Handling Unit | Indoor Unit | AHU - Indoor Unit ([Area Served]) | Air Handler is tracked as asset; other components are tracked in Sub Assets | On outside, visible for typical approach | An Air Handling Unit is a device containing a motor(s), fan(s), filters and heating and cooling coils. The unit usually contains a climate changer which also has a humidifier. The unit has both heating and cooling capabilities. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 73 00 | Indoor Central-Station Air-Handling Units | 23-33 25 13 11 | Customized Indoor Air Handling Units
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Air Handling Unit - Make-up Air Unit | D3050.50 - HVAC - Air Distribution | Air Handling Unit | Make-up Air Unit | D. HVAC - Air Handling - Air Handling Unit - Make-up Air Unit | D. HVAC - Air Handling | Air Handling Unit | Make-up Air Unit | AHU - Make-up Air Unit ([Area Served]) | Air Handler is tracked as asset; other components are tracked in Sub Assets | On outside, visible for typical approach | This device is used to make up air to space that typically has a large amount of exhaust such as a kitchen. Fan is a 100% outside air unit and normally is provided with a heating coil but can contain a cooling coil. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 73 23 | Custom Indoor Central-Station Air-Handling Units | 23-33 39 15 | Make Up Air Units
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Air Handling Unit - Roof Top Unit | D3050.50 - HVAC - Air Distribution | Air Handling Unit | Roof Top Unit | D. HVAC - Air Handling - Air Handling Unit - Roof Top Unit | D. HVAC - Air Handling | Air Handling Unit | Roof Top Unit | AHU - RTU ([Area Served]) | Air Handler is tracked as asset; other components are tracked in Sub Assets | On outside, visible for typical approach | This device is similar to an Air Handling Unit but is installed on the roof of a building. Contains supply fan(s), return fan(s), heating coils, VFD drives and cooling coils as well as controls for the unit. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 74 33 | Dedicated Outdoor-Air Units | 23-33 25 13 13 | Customized Rooftop Air Handling Units
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Clean Steam Generator | D3050.50 - HVAC - Air Distribution | Clean Steam Generator |  | D. HVAC - Air Handling - Clean Steam Generator | D. HVAC - Air Handling | Clean Steam Generator |  | Clean Steam Generator | Each Clean Steam Generator | On control panel | Typically steam to steam unit utilized to supply contaminant-free steam for clinical purposes. |  | 21-04 30 50 30 | Facility Steam Distribution | 22-23 84 13 29 | Self-Contained Steam Humidifiers | 23-33 27 15 | Air Humidifiers
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Condensate Pump | D3050.50 - HVAC - Air Distribution | Condensate Pump |  | D. HVAC - Air Handling - Condensate Pump | D. HVAC - Air Handling | Condensate Pump |  | Condensate Pump | Each unit | On control panel | This is a pump that is used in certain application to capture condensate from a cooling coil and pump it to a drain. Used in applications where gravity is not available for drainage such above the ceiling. These units need periodic inspections to prevent flooding. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 21 29 | Automatic Condensate Pump Units | 23-27 17 00 | Pumps
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Constant Air Volume Box | D3050.50 - HVAC - Air Distribution | Constant Air Volume Box |  | D. HVAC - Air Handling - Constant Air Volume Box | D. HVAC - Air Handling | Constant Air Volume Box |  | Constant Air Volume Box | Each unit | Place barcode on unit or ceiling grid | A terminal air distribution unit that employs an automated damper to provide a set volume of air. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 36 13
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Damper - Fire | D3050.50 - HVAC - Air Distribution | Damper | Fire | D. HVAC - Air Handling - Damper - Fire | D. HVAC - Air Handling | Damper | Fire | Damper - Fire | Each Damper | On damper housing (label on ceiling grid) | A fire damper works when the heat from the fire causes the normal temperature of a room to rise to about 165 degrees Fahrenheit. The fusible link attached to the damper would then melt, causing the damper's door to close. |  | 21-04 40 10 | Fire Suppression | 22-23 33 13 16 | Fire Dampers | 23-33 29 23 | Fire Dampers
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Damper - Fire/Smoke Combination | D3050.50 - HVAC - Air Distribution | Damper | Fire/Smoke Combination | D. HVAC - Air Handling - Damper - Fire/Smoke Combination | D. HVAC - Air Handling | Damper | Fire/Smoke Combination | Damper - Fire/Smoke Combination | Each Damper | On damper housing (label on ceiling grid) | Combination Fire/Smoke Dampers are used to prevent the passage of both fire and smoke. The damper closes by; the duct temperature reaches a high enough level to melt a fusible link or; it closes upon the detection of smoke which is sense by a nearby smoke detector.. |  | 21-04 40 10 | Fire Suppression | 22-23 33 13 16 | Fire Dampers
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Damper - Smoke | D3050.50 - HVAC - Air Distribution | Damper | Smoke | D. HVAC - Air Handling - Damper - Smoke | D. HVAC - Air Handling | Damper | Smoke | Damper - Smoke | Each Damper | On damper housing (label on ceiling grid) | Smoke dampers are activated by the fire alarm system, usually initiated by smoke detectors, or interlocked with a fire suppression system. Smoke dampers close by an electric or pneumatic actuator, or a spring actuator, and can be either manually reset or driven open on a reset signal to the electric or pneumatic actuator. |  | 21-04 40 10 | Fire Suppression | 22-23 33 13 19 | Smoke-Control Dampers | 23-33 29 25 | Smoke Dampers
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Damper - Type to be determined | D3050.50 - HVAC - Air Distribution | Damper | Type to be determined | D. HVAC - Air Handling - Damper - Type to be determined | D. HVAC - Air Handling | Damper | Type to be determined | Damper - Type to be determined | Each Damper | On damper housing (label on ceiling grid) | A damper is a valve or plate that stops or regulates the flow of air inside a duct, chimney, VAV box, air handler, or other air-handling equipment. |  | 21-04 40 10 | Fire Suppression | 22-23 33 13 16 | Fire Dampers
Asset | D3050.50 | Not on One-Line | D3050.50 - HVAC - Air Distribution - Dehumidifier | D3050.50 - HVAC - Air Distribution | Dehumidifier |  | D. HVAC - Air Handling - Dehumidifier | D. HVAC - Air Handling | Dehumidifier |  | Dehumidifier | Each unit (not if it is part of AHU) | On unit | A device for removing moisture from air by a mechanical or desiccant cycle. May be mounted as part of an air handling unit or a standalone unit. |  | 21-04 30 50 90 | Facility Distribution Systems Supplementary Components | 22-23 84 16 | Mechanical Dehumidification Units | 23-33 27 13 11 | Dehumidifiers
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Humidifier | D3050.50 - HVAC - Air Distribution | Humidifier |  | D. HVAC - Air Handling - Humidifier | D. HVAC - Air Handling | Humidifier |  | Humidifier | Each humidifier (if sub-asset to the AHU, then it should be merged with the AHU) | On control panel | A device that is used to add humidity to air. Normally part of an Air Handling Unit but can be installed in ductwork. |  | 21-04 30 50 90 | Facility Distribution Systems Supplementary Components | 22-23 84 13 | Humidifiers | 23-33 27 15 | Air Humidifiers
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Reheat Coil | D3050.50 - HVAC - Air Distribution | Reheat Coil |  | D. HVAC - Air Handling - Reheat Coil | D. HVAC - Air Handling | Reheat Coil |  | Reheat Coil | Each unit | Place barcode on unit or ceiling grid | A heating coil place in ductwork for temperature control. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 36 16 | Variable-Air-Volume Units | 23-33 41 17 13 | Variable Air Volume Terminal Units
Asset | D3050.50 | D30-5 | D3050.50 - HVAC - Air Distribution - Variable Air Volume Box | D3050.50 - HVAC - Air Distribution | Variable Air Volume Box |  | D. HVAC - Air Handling - Variable Air Volume Box | D. HVAC - Air Handling | Variable Air Volume Box |  | Variable Air Volume Box | Each unit | Place barcode on unit or ceiling grid | A terminal air distribution unit that employs an automated damper to vary the flow of air and therefore temperature in a space. |  | 21-04 30 50 50 | HVAC Air Distribution | 22-23 36 16 | Variable-Air-Volume Units | 23-33 41 17 13 | Variable Air Volume Terminal Units
Supplemental Elements | D3050.50.99 | n/a | D3050.50 - HVAC - Air Distribution - [Supplemental Elements] Air Distribution | D3050.50 - HVAC - Air Distribution | [Supplemental Elements] Air Distribution |  | D. HVAC - Air Handling - [Supplemental Elements] Air Distribution | D. HVAC - Air Handling | [Supplemental Elements] Air Distribution |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3060.10 |  | D3060 - HVAC - Ventilation | D3060 - HVAC - Ventilation |  |  | D. HVAC - Ventilation | D. HVAC - Ventilation | [5 empty] | General Category |  | 21-04 30 60 | Ventilation
Grouping | D3060.10 |  | D3060.10 - HVAC - Ventilation - Supply Air | D3060.10 - HVAC - Ventilation - Supply Air |  |  | D. HVAC - Ventilation - Supply Air | D. HVAC - Ventilation - Supply Air | [5 empty] | General Category |  | 21-04 30 60 | Ventilation
Asset | D3060.10 | D30-5 | D3060.10 - HVAC - Ventilation - Supply Air - Stairwell Pressurization Fan | D3060.10 - HVAC - Ventilation - Supply Air | Stairwell Pressurization Fan |  | D. HVAC - Ventilation - Supply Air - Stairwell Pressurization Fan | D. HVAC - Ventilation - Supply Air | Stairwell Pressurization Fan |  | Stairwell Pressurization Fan | Each Fan | On housing or panel | In case of a fire, clean outside air is forced by a stair pressurization fan into a stairwell. The pressurization is used to push back on smoke, keeping the smoke out of the escape route. |  | 21-04 30 60 10 | Supply Air | 22-23 34 00 | HVAC Fans | 23-33 31 19 | Fans
Asset | D3060.10 | D30-5 | D3060.10 - HVAC - Ventilation - Supply Air - Supply Air Fan | D3060.10 - HVAC - Ventilation - Supply Air | Supply Air Fan |  | D. HVAC - Ventilation - Supply Air - Supply Air Fan | D. HVAC - Ventilation - Supply Air | Supply Air Fan |  | Supply Air Fan | This is typically part of the AHU. | On housing or panel | Fan typically associated with AHU to push air into occupant spaces. |  | 21-04 30 60 10 | Supply Air | 22-23 34 00 | HVAC Fans | 23-33 31 19 | Fans
Asset | D3060.10 | D30-5 | D3060.10 - HVAC - Ventilation - Supply Air - Transfer Fan | D3060.10 - HVAC - Ventilation - Supply Air | Transfer Fan |  | D. HVAC - Ventilation - Supply Air - Transfer Fan | D. HVAC - Ventilation - Supply Air | Transfer Fan |  | Transfer Fan | Each Fan | On housing or panel | Similar in configuration to supply fan, but transfers air between plenums or spaces and is typically independent of packaged AHU. Added back in as Unit CME 10/24/17. |  | 21-04 30 60 10 | Supply Air | 22-23 34 00 | HVAC Fans | 23-33 31 19 | Fans
Supplemental Elements | D3060.10.99 | n/a | D3060 - HVAC - Ventilation - [Supplemental Elements] Ventilation | D3060 - HVAC - Ventilation | [Supplemental Elements] Ventilation |  | D. HVAC - Ventilation - [Supplemental Elements] Ventilation | D. HVAC - Ventilation | [Supplemental Elements] Ventilation |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3060.20 |  | D3060.20 - HVAC - Ventilation - Return Air | D3060.20 - HVAC - Ventilation - Return Air |  |  | D. HVAC - Ventilation - Return Air | D. HVAC - Ventilation - Return Air | [5 empty] | General Category |  | 21-04 30 60 | Ventilation
Asset | D3060.20 | D30-5 | D3060.20 - HVAC - Ventilation - Return Air - Return Air Fan | D3060.20 - HVAC - Ventilation - Return Air | Return Air Fan |  | D. HVAC - Ventilation - Return Air - Return Air Fan | D. HVAC - Ventilation - Return Air | Return Air Fan |  | Return Air Fan | This is typically part of the AHU. | On housing or panel | Fan typically associated with AHU to draw air from occupant spaces and either discharge it to the exterior or return it back to the AHU. |  | 21-04 30 60 20 | Return Air | 22-23 34 00 | HVAC Fans | 23-33 31 19 | Fans
Grouping | D3060.30 |  | D3060.30 - HVAC - Ventilation - Exhaust Air | D3060.30 - HVAC - Ventilation - Exhaust Air |  |  | D. HVAC - Ventilation - Exhaust Air | D. HVAC - Ventilation - Exhaust Air | [5 empty] | General Category |  | 21-04 30 60 | Ventilation
System | D3060.30 | D30-5 | D3060.30 - HVAC - Ventilation - Exhaust Air - (System) Exhaust Air | D3060.30 - HVAC - Ventilation - Exhaust Air | (System) Exhaust Air |  | D. HVAC - Ventilation - Exhaust Air - (System) Exhaust Air | D. HVAC - Ventilation - Exhaust Air | (System) Exhaust Air |  | SYS Exhaust Air ([Area Served]) | Each system | No barcode - Track by location | Generic representation of system. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan |  | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan |  | Exhaust Fan ([Area served]) | Each Fan | On housing or panel | Use this category if you are not sure about the exact function of the exhaust fan. |  | 21-04 30 60 30 | Exhaust Air | 22-23 34 00 | HVAC Fans | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan - Helium | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan | Helium | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan - Helium | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan | Helium | Exhaust Fan - Helium ([Area served]) | Each Fan | On housing or panel | This fan is used to vent helium from an MRI machine in case of sudden venting of this gas, which is used to cool the magnet. It is activated by a helium sensor. |  | 21-04 30 60 30 | Exhaust Air | 22-23 35 00 | Special Exhaust Systems | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan - HEPA Filtered | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan | HEPA Filtered | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan - HEPA Filtered | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan | HEPA Filtered | Exhaust Fan - HEPA Filtered ([Area served]) | Each unit | On housing or panel | This is a high-efficiency particulate air (HEPA) which is an air filter element that must remove 99.97% (ASME, U.S. DOE) of particles whose diameter is greater than or equal to 0.3 μm. These are normally installed as a terminal device in or near the room they serve. |  | 21-04 30 60 30 | Exhaust Air | 22-23 35 00 | Special Exhaust Systems | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan - Isolation | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan | Isolation | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan - Isolation | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan | Isolation | Exhaust Fan - Isolation ([Area served]) | Each Fan | On housing or panel | An exhaust fan used to ventilate airborne biohazards from isolation rooms or other areas. Exhaust is normally located 25ft from nearest intake or operable window. |  | 21-04 30 60 30 | Exhaust Air | 22-23 35 00 | Special Exhaust Systems | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan - Kitchen Hood | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan | Kitchen Hood | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan - Kitchen Hood | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan | Kitchen Hood | Exhaust Fan - Kitchen ([Area served]) | Each Fan | On housing or panel | A fan used to exhaust cooking fumes from a kitchen area. Provided with a hood and a means to trap grease. |  | 21-04 30 60 30 | Exhaust Air | 22-23 35 00 | Special Exhaust Systems | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan - Laboratory / Biohazard | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan | Laboratory / Biohazard | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan - Laboratory / Biohazard | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan | Laboratory / Biohazard | Exhaust Fan - Laboratory / Biohazard ([Area served]) | Each Fan | On housing or panel | An exhaust fan typically connected to a fume hood in a laboratory to exhaust chemicals and other hazardous contaminants. Exhaust is normally located 25ft from nearest intake or operable window. |  | 21-04 30 60 30 | Exhaust Air | 22-23 35 00 | Special Exhaust Systems | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan - Radiology | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan | Radiology | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan - Radiology | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan | Radiology | Exhaust Fan - Radiology ([Area served]) | Each Fan | On housing or panel | An exhaust fan connected to a radiology area of a hospital to maintain the proper pressurization and air changes per hour. |  | 21-04 30 60 30 | Exhaust Air | 22-23 35 00 | Special Exhaust Systems | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan - Smoke Purge | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan | Smoke Purge | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan - Smoke Purge | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan | Smoke Purge | Exhaust Fan - Smoke Purge ([Area served]) | Each Fan | On housing or panel | A fan dedicated to exhausting spaces that is activated by the fire alarm system to purge smoke from the interior of the facility. |  | 21-04 30 60 30 | Exhaust Air | 22-23 35 00 | Special Exhaust Systems | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Exhaust Fan - Toilet | D3060.30 - HVAC - Ventilation - Exhaust Air | Exhaust Fan | Toilet | D. HVAC - Ventilation - Exhaust Air - Exhaust Fan - Toilet | D. HVAC - Ventilation - Exhaust Air | Exhaust Fan | Toilet | Exhaust Fan - Toilet ([Area served]) | Each Fan | On housing or panel | An exhaust fan connected to a bathroom to maintain ventilation. |  | 21-04 30 60 30 | Exhaust Air | 22-23 34 00 | HVAC Fans | 23-33 31 19 | Fans
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Kitchen Hood | D3060.30 - HVAC - Ventilation - Exhaust Air | Kitchen Hood |  | D. HVAC - Ventilation - Exhaust Air - Kitchen Hood | D. HVAC - Ventilation - Exhaust Air | Kitchen Hood |  | Kitchen Hood ([Area served]) | Each hood | Located on Hood, visible, without being exposed to heat | An exhaust hood, extractor hood, or range hood is a device containing a mechanical fan that hangs above the stove or cooktop in the kitchen. It removes airborne grease, combustion products, fumes, smoke, odors, heat, and steam from the air by evacuation of the air and filtration. |  | 21-04 30 60 30 | Exhaust Air | 22-23 38 13 | Commercial-Kitchen Hoods | 23-33 31 15 21 | Grease Exhaust Hoods
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Kitchen Hood - Wash System | D3060.30 - HVAC - Ventilation - Exhaust Air | Kitchen Hood | Wash System | D. HVAC - Ventilation - Exhaust Air - Kitchen Hood - Wash System | D. HVAC - Ventilation - Exhaust Air | Kitchen Hood | Wash System | Kitchen Hood Wash System | Each hood | Located on Hood, visible, without being exposed to heat | An exhaust hood, extractor hood, or range hood is a device containing a mechanical fan that hangs above the stove or cooktop in the kitchen. It removes airborne grease, combustion products, fumes, smoke, odors, heat, and steam from the air by evacuation of the air and filtration. |  | 21-04 30 60 30 | Exhaust Air | 22-23 38 13 | Commercial-Kitchen Hoods | 23-33 31 15 | Exhaust Hoods
Asset | D3060.30 | Not on One-Line | D3060.30 - HVAC - Ventilation - Exhaust Air - Laundry Dryer Exhaust Vent | D3060.30 - HVAC - Ventilation - Exhaust Air | Laundry Dryer Exhaust Vent |  | D. HVAC - Ventilation - Exhaust Air - Laundry Dryer Exhaust Vent | D. HVAC - Ventilation - Exhaust Air | Laundry Dryer Exhaust Vent |  | Laundry Dryer Exhaust Vent | Each Fan | On housing or panel | This is the ductwork and lint capture system that is connected a dryer or dryers to capture lint and discharge the exhaust to the exterior of a building. |  | 21-04 30 60 30 | Exhaust Air | 22-23 35 00 | Special Exhaust Systems | 23-33 49 25 11 | Exhaust Air Ventilation Registers
Supplemental Elements | D3060.30.99 | n/a | D3060.30 - HVAC - Ventilation - Exhaust Air - [Supplemental Elements] Exhaust Air | D3060.30 - HVAC - Ventilation - Exhaust Air | [Supplemental Elements] Exhaust Air |  | D. HVAC - Ventilation - Exhaust Air - [Supplemental Elements] Exhaust Air | D. HVAC - Ventilation - Exhaust Air | [Supplemental Elements] Exhaust Air |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D3060.70 |  | D3060.70 - HVAC - Ventilation - Air Cleaning | D3060.70 - HVAC - Ventilation - Air Cleaning |  |  | D. HVAC - Ventilation - Air Cleaning | D. HVAC - Ventilation - Air Cleaning | [5 empty] | General Category |  | 21-04 30 60 | Ventilation | 22-23 40 00 | HVAC Air Cleaning Devices
Asset | D3060.70 | D30-5 | D3060.70 - HVAC - Ventilation - Air Cleaning - HEPA Filter Rack | D3060.70 - HVAC - Ventilation - Air Cleaning | HEPA Filter Rack |  | D. HVAC - Ventilation - Air Cleaning - HEPA Filter Rack | D. HVAC - Ventilation - Air Cleaning | HEPA Filter Rack |  | HEPA Filter Rack | Each unit, only if standalone | On unit | Is part of Air Handler, but has its own ITM requirements; is typically tracked as a component of the AHU |  | 21-04 30 60 70 | HVAC Air Cleaning | 22-23 41 33 | High-Efficiency Particulate Filtration | 23-27 57 27 17 | HEPA Filters
Asset | D3060.70 | D30-5 | D3060.70 - HVAC - Ventilation - Air Cleaning - Non-HEPA Filter Rack | D3060.70 - HVAC - Ventilation - Air Cleaning | Non-HEPA Filter Rack |  | D. HVAC - Ventilation - Air Cleaning - Non-HEPA Filter Rack | D. HVAC - Ventilation - Air Cleaning | Non-HEPA Filter Rack |  | Non-HEPA Filter Rack | Each unit, only if standalone | On unit | A rack integral with the air handling unit that allows replaceable filter media to be placed in the air stream; is typically tracked as a component of the AHU |  | 21-04 30 60 70 | HVAC Air Cleaning | 22-23 41 00 | Particulate Air Filtration | 23-27 57 27 11 | Air Filter Components
Asset | D3060.70 | Not on One-Line | D3060.70 - HVAC - Ventilation - Air Cleaning - Portable HEPA Filter | D3060.70 - HVAC - Ventilation - Air Cleaning | Portable HEPA Filter |  | D. HVAC - Ventilation - Air Cleaning - Portable HEPA Filter | D. HVAC - Ventilation - Air Cleaning | Portable HEPA Filter |  | Portable HEPA Filter | Each unit | On unit | A unitary, mobile air handling device consisting of a blower to draw space air through a HEPA filter for recirculation of space air or discharge out of the space.
Asset | D3060.70 | Not on One-Line | D3060.70 - HVAC - Ventilation - Air Cleaning - Saw Dust Filter | D3060.70 - HVAC - Ventilation - Air Cleaning | Saw Dust Filter |  | D. HVAC - Ventilation - Air Cleaning - Saw Dust Filter | D. HVAC - Ventilation - Air Cleaning | Saw Dust Filter |  | Saw Dust Filter | Each unit, only if standalone | On unit | This device is used by the Carpentry Shop to capture dust from wood cutting machines. |  | 21-04 30 60 70 | HVAC Air Cleaning | 22-23 35 13 13 | Sawdust Collection Systems | 23-27 57 29 | Dust Collectors
Asset | D3060.70 | Not on One-Line | D3060.70 - HVAC - Ventilation - Air Cleaning - Washable Aluminum Filter | D3060.70 - HVAC - Ventilation - Air Cleaning | Washable Aluminum Filter |  | D. HVAC - Ventilation - Air Cleaning - Washable Aluminum Filter | D. HVAC - Ventilation - Air Cleaning | Washable Aluminum Filter |  | Washable Aluminum Filter | Each unit, only if standalone | On unit | Is used for laundry (dryer) discharge. |  | 21-04 30 60 70 | HVAC Air Cleaning | 22-23 41 19 | Washable Air Filters | 23-27 57 27 | Air Filters
Grouping | D3070.10 |  | D3070.10 - HVAC - Snow Melting | D3070.10 - HVAC - Snow Melting |  |  | D. HVAC - Snow Melting | D. HVAC - Snow Melting | [5 empty] | General Category |  | 21-04 30 70 10 | Snow Melting | 22-23 83 00
System | D3070.10 | Not on One-Line | D3070.10 - HVAC - Snow Melting - (System) Snow Melting | D3070.10 - HVAC - Snow Melting | (System) Snow Melting |  | D. HVAC - Snow Melting - (System) Snow Melting | D. HVAC - Snow Melting | (System) Snow Melting |  | SYS Snow Melting ([Area Served]) | Each system | Track by location served | This is a system that normally consists of a heat exchanger, pumps, piping and controls. Piping is installed under sidewalks and/or driveways to keep same free of ice and snow. |  | 21-04 30 70 10 | Snow Melting | 22-32 17 43 | Pavement Snow Melting Systems
Supplemental Elements | D3070.10.99 | n/a | D3070.10 - HVAC - Snow Melting - [Supplemental Elements] Snow Melting | D3070.10 - HVAC - Snow Melting | [Supplemental Elements] Snow Melting |  | D. HVAC - Snow Melting - [Supplemental Elements] Snow Melting | D. HVAC - Snow Melting | [Supplemental Elements] Snow Melting |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D4010.10 |  | D4010.10 - Fire Protection, Water-Based | D4010.10 - Fire Protection, Water-Based |  |  | D. Fire Protection, Water-Based | D. Fire Protection, Water-Based | [5 empty] | General Category |  | 21-04 40 10 10 | Water-Based Fire-Suppression | 22-21 10 00 | Water-Based Fire-Suppression Systems | 23-29 33 11 | Water Based Suppression Equipment
System | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - (System) Sprinkler, Dry Pipe | D4010.10 - Fire Protection, Water-Based | (System) Sprinkler, Dry Pipe |  | D. Fire Protection, Water-Based - (System) Sprinkler, Dry Pipe | D. Fire Protection, Water-Based | (System) Sprinkler, Dry Pipe |  | SYS Sprinkler, Dry Pipe ([Area Served]) | Generic asset | On control panel | Sprinkler system in which the branch lines to occupied spaces are pressurized. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 13 16 | Dry-Pipe Sprinkler Systems | 23-29 33 11 11 13 | Dry Pendant Sprinkler Heads
System | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - (System) Sprinkler, Pre-action | D4010.10 - Fire Protection, Water-Based | (System) Sprinkler, Pre-action |  | D. Fire Protection, Water-Based - (System) Sprinkler, Pre-action | D. Fire Protection, Water-Based | (System) Sprinkler, Pre-action |  | SYS Sprinkler, Pre-Action ([Area Served]) | Generic asset | On control panel | Sprinkler system in which inadvertent/accidental activation is highly problematic. These are interlocked with fire control systems and require a "preceding" event to release. Can be wet, dry or deluge design. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 13 19 | Pre-action Sprinkler Systems | 23-29 33 11 | Water Based Suppression Equipment
System | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - (System) Sprinkler, Wet Pipe | D4010.10 - Fire Protection, Water-Based | (System) Sprinkler, Wet Pipe |  | D. Fire Protection, Water-Based - (System) Sprinkler, Wet Pipe | D. Fire Protection, Water-Based | (System) Sprinkler, Wet Pipe |  | SYS Sprinkler, Wet Pipe ([Area Served]) | Generic asset | On control panel | Sprinkler system in which the branch lines to occupied spaces are dry and unpressurized; usually for use in areas susceptible to freeze damage. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 13 13 | Wet-Pipe Sprinkler Systems | 23-29 33 11 11 11 | Wet Pendant Sprinkler Heads
System | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - (System) Standpipe | D4010.10 - Fire Protection, Water-Based | (System) Standpipe |  | D. Fire Protection, Water-Based - (System) Standpipe | D. Fire Protection, Water-Based | (System) Standpipe |  | SYS Standpipe ([Area Served]) | Each standpipe | Track by staircase ID | An arrangement of piping, valves, hose connections, and allied equipment installed in a building or structure, with the hose connections located in such a manner that water can be discharged in streams or spray patterns through attached hose and nozzles, for the purpose of extinguishing a fire, thereby protecting a building or structure and its contents in addition to protecting the occupants. A sprinkler standpipe is connected to flow control assemblies that feed sprinkler zones throughout a structure. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 00 | Fire-Suppression Standpipes | 23-29 25 15 19 11 | Fire Fighting Standpipes
System | D4010.10 | Not on One-Line | D4010.10 - Fire Protection, Water-Based - (System) Water Mist Extinguishing | D4010.10 - Fire Protection, Water-Based | (System) Water Mist Extinguishing |  | D. Fire Protection, Water-Based - (System) Water Mist Extinguishing | D. Fire Protection, Water-Based | (System) Water Mist Extinguishing |  | SYS Sprinkler, Dry Pipe ([Area Served]) | Generic asset | On control panel | A fire extinguisher containing distilled or de-ionized water and employing a nozzle that discharges the agent in a fine spray. |  | 21-04 40 10 50 | Fire-Extinguishing | 22-21 20 00 | Fire-Extinguishing Systems | 23-29 33 11 19 | Water Mist Systems
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Alarm Check Valve | D4010.10 - Fire Protection, Water-Based | Alarm Check Valve |  | D. Fire Protection, Water-Based - Alarm Check Valve | D. Fire Protection, Water-Based | Alarm Check Valve |  | Alarm Check Valve | Each alarm valve | On tag, or nameplate | A vertical check valve utilized in a sprinkler system to prevent reverse water flow and provide alarm upon a predetermined water flow rate. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 23 | Fire-Suppression Hose Valves | 23-27 31 00 | Valves
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Backflow Preventer - Fire Protection | D4010.10 - Fire Protection, Water-Based | Backflow Preventer - Fire Protection |  | D. Fire Protection, Water-Based - Backflow Preventer - Fire Protection | D. Fire Protection, Water-Based | Backflow Preventer - Fire Protection |  | Fire Protection | Each backflow preventer | On tag chained to backflow preventer | This device is required wherever potable water systems are piped into non-potable systems. These plumbing fixtures sense conditions wherein the non-potable system pressure exceeds the potable system, raising the potential for contamination, and triggering a disconnection of the two systems, along with a dumping of flow. |  | 21-07 30 10 30 | Site Fire Protection Water Distribution | 22-21 11 00 | Facility Fire-Suppression Water-Service Piping | 23-27 31 11 | Backflow Preventors
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Combo Inspector Test/Drain Valve | D4010.10 - Fire Protection, Water-Based | Combo Inspector Test/Drain Valve |  | D. Fire Protection, Water-Based - Combo Inspector Test/Drain Valve | D. Fire Protection, Water-Based | Combo Inspector Test/Drain Valve |  | Combo Inspector Test/Drain Valve | Each valve | On tag chained to drain | This valve is used to verify that the water flow alarm on a sprinkler system is operational. The inspector's test connection can be located anywhere downstream of the main control valve on a wet pipe system, and must be located on the highest, most remote branch line of a dry pipe system. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 23 | Fire-Suppression Hose Valves | 23-27 31 00 | Valves
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Control Valve | D4010.10 - Fire Protection, Water-Based | Control Valve |  | D. Fire Protection, Water-Based - Control Valve | D. Fire Protection, Water-Based | Control Valve |  | Control Valve | Each control valve | On tag, chained to valve | The primary isolation valve for a standpipe or sprinkler system. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 23 | Fire-Suppression Hose Valves | 23-27 31 00 | Valves
Asset | D4010.10 | D40-1b | D4010.10 - Fire Protection, Water-Based - FDC Check Valve | D4010.10 - Fire Protection, Water-Based | FDC Check Valve |  | D. Fire Protection, Water-Based - FDC Check Valve | D. Fire Protection, Water-Based | FDC Check Valve |  | FDC Check Valve | Each valve | On tag, chained to valve | This valve is installed at a fire department connection to prevent flow of water from the system to the FDC. When a fire truck connects to the fire department connection the water will flow in one direction from the FDC to the system it services. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 23 | Fire-Suppression Hose Valves | 23-27 31 19 | Check Valves
Asset | D4010.10 | D40-1b | D4010.10 - Fire Protection, Water-Based - Fire Department Siamese Connection | D4010.10 - Fire Protection, Water-Based | Fire Department Siamese Connection |  | D. Fire Protection, Water-Based - Fire Department Siamese Connection | D. Fire Protection, Water-Based | Fire Department Siamese Connection |  | Fire Department Siamese Connection | Each Connection | High-strength barcode on bottom of FDC | A Siamese connection or splitter in fire protection engineering is a pipe fitting that allows two or more fire hoses to be connected to a single standpipe riser at the same general location. Normally installed at street level and color coded to indicate which system it's tied to. Red for standpipe, Green for Sprinkler and Yellow for combination standpipe/sprinkler. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 11 19 | Fire-Department Connections | 23-29 25 15 19 | Fire Hose Connectors
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Fire Hose Cabinet / Rack | D4010.10 - Fire Protection, Water-Based | Fire Hose Cabinet / Rack |  | D. Fire Protection, Water-Based - Fire Hose Cabinet / Rack | D. Fire Protection, Water-Based | Fire Hose Cabinet / Rack |  | Fire Hose Cabinet / Rack | Each Cabinet | Inside of Cabinet | An enclosure to house a fire service hose connection and hose with nozzle. May include a hose wrench. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 13 | Fire-Suppression Hoses and Nozzles | 23-29 25 15 15 | Cabinets for Fire Hoses
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Fire Hose Connection | D4010.10 - Fire Protection, Water-Based | Fire Hose Connection |  | D. Fire Protection, Water-Based - Fire Hose Connection | D. Fire Protection, Water-Based | Fire Hose Connection |  | Fire Hose Connection | Each Connection | On connection or on piping coming into connection (if surface is smoother than connection) | A point of connection for a fire hose that meets the requirements of NFPA 1963. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 13 | Fire-Suppression Hoses and Nozzles | 23-29 25 15 19 | Fire Hose Connectors
Asset | D4010.10 | D40-1b | D4010.10 - Fire Protection, Water-Based - Fire Pump | D4010.10 - Fire Protection, Water-Based | Fire Pump |  | D. Fire Protection, Water-Based - Fire Pump | D. Fire Protection, Water-Based | Fire Pump |  | Fire Pump | Each unit | On control panel | Dedicated pump taking city water supply to pressurize firefighting (sprinkler system, etc..) water risers and branch piping. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 30 00 | Fire Pumps | 23-27 17 00 | Pumps
Asset | D4010.10 | D40-1b | D4010.10 - Fire Protection, Water-Based - Fire Pump - Diesel | D4010.10 - Fire Protection, Water-Based | Fire Pump | Diesel | D. Fire Protection, Water-Based - Fire Pump - Diesel | D. Fire Protection, Water-Based | Fire Pump | Diesel | Fire Pump - Diesel | Each unit | On control panel | Dedicated diesel-powered pump drawing water from a municipal supply or on-site tank to pressurize firefighting (sprinkler system, etc..) water risers and branch piping.
Asset | D4010.10 | D40-1b | D4010.10 - Fire Protection, Water-Based - Fire Pump - Electric | D4010.10 - Fire Protection, Water-Based | Fire Pump | Electric | D. Fire Protection, Water-Based - Fire Pump - Electric | D. Fire Protection, Water-Based | Fire Pump | Electric | Fire Pump - Electric | Each unit | On control panel | Dedicated electrical pump drawing water from a municipal supply or on-site tank to pressurize firefighting (sprinkler system, etc..) water risers and branch piping.
Asset | D4010.10 | D40-1c | D4010.10 - Fire Protection, Water-Based - Fire Water Storage Tank | D4010.10 - Fire Protection, Water-Based | Fire Water Storage Tank |  | D. Fire Protection, Water-Based - Fire Water Storage Tank | D. Fire Protection, Water-Based | Fire Water Storage Tank |  | Fire Water Storage Tank | Each tank | On control panel, if no panel on dunnage under tower | Tank storing water, used for fire suppression. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 41 00 | Storage Tanks for Fire-Suppression Water | 23-27 29 19 | Tanks
Asset | D4010.10 | D40-1b | D4010.10 - Fire Protection, Water-Based - Jockey Fire Pump | D4010.10 - Fire Protection, Water-Based | Jockey Fire Pump |  | D. Fire Protection, Water-Based - Jockey Fire Pump | D. Fire Protection, Water-Based | Jockey Fire Pump |  | Jockey Fire Pump | Each Pump | On pump set control panel | A jockey pump is a small pump connected to a fire-sprinkler system to maintain pressure in the sprinkler pipes. This is to ensure that if a fire-sprinkler is activated, there will be a pressure drop, which will be sensed by the fire pumps automatic controller, which will cause the fire pump to start. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 30 00 | Fire Pumps | 23-29 31 35 | Jockey Pump Controllers
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Low-point drains for dry pipe system/Drum Drip | D4010.10 - Fire Protection, Water-Based | Low-point drains for dry pipe system/Drum Drip |  | D. Fire Protection, Water-Based - Low-point drains for dry pipe system/Drum Drip | D. Fire Protection, Water-Based | Low-point drains for dry pipe system/Drum Drip |  | Low-point drains for dry pipe system/Drum Drip | Each low point | On tag chained to low point | Drain valve that allows water to be removed from the normally dry lines after testing or used to prevent freezing. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 13 16 | Dry-Pipe Sprinkler Systems
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Main Drain Valve | D4010.10 - Fire Protection, Water-Based | Main Drain Valve |  | D. Fire Protection, Water-Based - Main Drain Valve | D. Fire Protection, Water-Based | Main Drain Valve |  | Main Drain Valve | Each valve | On tag chained to drain | The primary drain connection located on the system riser and also utilized as a flow test connection. The main drain test serves as a tool in evaluating the condition of the water supply to a fire-sprinkler system. It is intended to reveal any deterioration of the water supply by comparing the test results to those of previous test results. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 23 | Fire-Suppression Hose Valves | 23-27 31 00 | Valves
Asset | D4010.10 | D40-1c | D4010.10 - Fire Protection, Water-Based - Private Fire Hydrants | D4010.10 - Fire Protection, Water-Based | Private Fire Hydrants |  | D. Fire Protection, Water-Based - Private Fire Hydrants | D. Fire Protection, Water-Based | Private Fire Hydrants |  | Private Fire Hydrants | Each hydrant | High-strength barcode on hydrant | A hydrant generally of the same design as utilized on public systems but located on private property and maintained by the owner. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 11 16 | Facility Fire Hydrants | 23-29 25 13 | Fire Hydrants
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Riser Drain Valve | D4010.10 - Fire Protection, Water-Based | Riser Drain Valve |  | D. Fire Protection, Water-Based - Riser Drain Valve | D. Fire Protection, Water-Based | Riser Drain Valve |  | Riser Drain Valve | Each Valve | On valve or valve tag | This is a valve installed on the fire protection riser that allows the riser to be drained for maintenance or testing purposes. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 23 | Fire-Suppression Hose Valves | 23-27 31 00 | Valves
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler - Air Compressor | D4010.10 - Fire Protection, Water-Based | Sprinkler - Air Compressor |  | D. Fire Protection, Water-Based - Sprinkler - Air Compressor | D. Fire Protection, Water-Based | Sprinkler - Air Compressor |  | Air Compressor | Each Device | On control panel | A compressor that is used to maintain air pressure in a dry pipe sprinkler system. In these systems air is used instead of water to maintain system pressure to prevent the sprinkler pipes, which are installed in open areas like a parking garage or loading dock, from freezing. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 13 00 | Fire-Suppression Sprinkler Systems | 23-27 21 00 | Compressors
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler - Gauges (dry, pre-action and deluge) | D4010.10 - Fire Protection, Water-Based | Sprinkler - Gauges (dry, pre-action and deluge) |  | D. Fire Protection, Water-Based - Sprinkler - Gauges (dry, pre-action and deluge) | D. Fire Protection, Water-Based | Sprinkler - Gauges (dry, pre-action and deluge) |  | Gauges (dry, pre-action and deluge) | Each gauge | On device (not on face) | A standard pressure gauge for indicating fire system pressure. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 05 19 | Meters and Gages for Fire-Suppression Systems | 23-29 25 19 17 11 | Gas Cart Fire Extinguishers With Gauge
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler - Gauges (wet pipe systems) | D4010.10 - Fire Protection, Water-Based | Sprinkler - Gauges (wet pipe systems) |  | D. Fire Protection, Water-Based - Sprinkler - Gauges (wet pipe systems) | D. Fire Protection, Water-Based | Sprinkler - Gauges (wet pipe systems) |  | Gauges (wet pipe systems) | Each gauge | On device (not on face) | A standard pressure gauge for determining system pressure and treated as an asset based on inspection and service requirements. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 05 19 | Meters and Gages for Fire-Suppression Systems | 23-29 25 19 11 11 | Stored Pressure Fire Extinguishers With Gauge
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler - Hydraulic Nameplate | D4010.10 - Fire Protection, Water-Based | Sprinkler - Hydraulic Nameplate |  | D. Fire Protection, Water-Based - Sprinkler - Hydraulic Nameplate | D. Fire Protection, Water-Based | Sprinkler - Hydraulic Nameplate |  | Hydraulic Nameplate | Each Nameplate | On nameplate | A data plate affixed to the fire-sprinkler system providing design data. Treated as an asset so its condition can be periodically determined. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 05 53 | Identification for Fire-Suppression Piping and Equipment
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler - Main Shutoff Valve | D4010.10 - Fire Protection, Water-Based | Sprinkler - Main Shutoff Valve |  | D. Fire Protection, Water-Based - Sprinkler - Main Shutoff Valve | D. Fire Protection, Water-Based | Sprinkler - Main Shutoff Valve |  | Main Shutoff Valve | Each valve | On tag, chained to valve | The primary isolation valve for the sprinkler system. Secondary risers with isolation points can be downstream. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 23 | Fire-Suppression Hose Valves | 23-27 31 00 | Valves
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler - Pressure Reducing Valve (Fire Suppression) | D4010.10 - Fire Protection, Water-Based | Sprinkler - Pressure Reducing Valve (Fire Suppression) |  | D. Fire Protection, Water-Based - Sprinkler - Pressure Reducing Valve (Fire Suppression) | D. Fire Protection, Water-Based | Sprinkler - Pressure Reducing Valve (Fire Suppression) |  | Pressure Reducing Valve (Fire Suppression) | Each valve | On tag, chained to valve | A valve designed for the purpose of reducing the downstream water pressure under both flowing (residual) and nonflowing (static) conditions. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 12 23 | Fire-Suppression Hose Valves | 23-27 31 49 11 | Pressure Relief Valves
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler - Water Flow Switch | D4010.10 - Fire Protection, Water-Based | Sprinkler - Water Flow Switch |  | D. Fire Protection, Water-Based - Sprinkler - Water Flow Switch | D. Fire Protection, Water-Based | Sprinkler - Water Flow Switch |  | Water Flow Switch | Each Device | On device housing | A mechanical-to-electrical fire alarm input device; it tells the fire alarm system that water is flowing in the sprinkler system. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 13 13 | Wet-Pipe Sprinkler Systems | 23-29 29 15 | Fire Switches
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler - Water Motor Gong | D4010.10 - Fire Protection, Water-Based | Sprinkler - Water Motor Gong |  | D. Fire Protection, Water-Based - Sprinkler - Water Motor Gong | D. Fire Protection, Water-Based | Sprinkler - Water Motor Gong |  | Water Motor Gong | Each Device | On device housing | A large, wall-mounted bell that uses a clapper attached to a paddle wheel to make it ring. |  | 21-04 40 10 90 | Fire Suppression Supplementary Components | 22-21 13 13 | Wet-Pipe Sprinkler Systems
Asset | D4010.10 | D40-1a | D4010.10 - Fire Protection, Water-Based - Sprinkler Head Cabinet | D4010.10 - Fire Protection, Water-Based | Sprinkler Head Cabinet |  | D. Fire Protection, Water-Based - Sprinkler Head Cabinet | D. Fire Protection, Water-Based | Sprinkler Head Cabinet |  | Sprinkler Head Cabinet | Each cabinet | On casing | As per NFPA this is a cabinet of at least six spare sprinklers, which shall be maintained on the premises so that any sprinklers that have operated or been damaged in any way can be promptly replaced. In addition, a minimum of two sprinklers of each type and temperature rating should be provided. |  | 21-04 40 30 10 | Fire Protection Cabinets | 22-10 44 13 | Fire-Suppression Sprinkler Systems
Supplemental Elements | D4010.10.99 | n/a | D4010.10 - Fire Protection, Water-Based - [Supplemental Elements] Water-Based Fire Suppression | D4010.10 - Fire Protection, Water-Based | [Supplemental Elements] Water-Based Fire Suppression |  | D. Fire Protection, Water-Based - [Supplemental Elements] Water-Based Fire Suppression | D. Fire Protection, Water-Based | [Supplemental Elements] Water-Based Fire Suppression |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D4010.50 |  | D4010.50 - Fire Protection, Non-Water-Based | D4010.50 - Fire Protection, Non-Water-Based |  |  | D. Fire Protection, Non-Water-Based | D. Fire Protection, Non-Water-Based | [5 empty] | General Category |  |  |  | 22-21 24 00 | Dry-Chemical Fire-Extinguishing Systems | 23-29 33 13 | Non Water Based Suppression Equipment
System | D4010.50 | Not on One-Line | D4010.50 - Fire Protection, Non-Water-Based - (System) Dry Chemical Extinguishing | D4010.50 - Fire Protection, Non-Water-Based | (System) Dry Chemical Extinguishing |  | D. Fire Protection, Non-Water-Based - (System) Dry Chemical Extinguishing | D. Fire Protection, Non-Water-Based | (System) Dry Chemical Extinguishing |  | SYS Dry Chemical Extinguishing ([Area Served]) | Each System | Track by location | An installed system using a chemical agent that is automatically activated to suppress a specific area such as a kitchen hood or paint booth. |  | 21-04 40 10 50 | Fire-Extinguishing | 22-21 24 00 | Dry-Chemical Fire-Extinguishing Systems | 23-29 33 13 19 | Dry Chemical Fire Suppression Equipment
System | D4010.50 | Not on One-Line | D4010.50 - Fire Protection, Non-Water-Based - (System) Gaseous Extinguishing | D4010.50 - Fire Protection, Non-Water-Based | (System) Gaseous Extinguishing |  | D. Fire Protection, Non-Water-Based - (System) Gaseous Extinguishing | D. Fire Protection, Non-Water-Based | (System) Gaseous Extinguishing |  | SYS Gaseous Extinguishing ([Area Served]) | Each System | Track by location | A permanently installed suppression system with an agent such as carbon dioxide or FM200 utilized to protect specific equipment or spaces. |  | 21-04 40 10 50 | Fire-Extinguishing | 22-21 21 00 | Carbon-Dioxide Fire-Extinguishing Systems | 23-29 33 13 11 | Clean Agent Gaseous Suppression Equipment
System | D4010.50 | Not on One-Line | D4010.50 - Fire Protection, Non-Water-Based - (System) Kitchen Extinguishing | D4010.50 - Fire Protection, Non-Water-Based | (System) Kitchen Extinguishing |  | D. Fire Protection, Non-Water-Based - (System) Kitchen Extinguishing | D. Fire Protection, Non-Water-Based | (System) Kitchen Extinguishing |  | SYS Kitchen Extinguishing ([Area Served]) | Each System | Track by location | A permanently installed suppression system often using a wet agent for suppression of fires on grills and stoves. |  | 21-04 40 10 50 | Fire-Extinguishing | 22-21 20 00 | Fire-Extinguishing Systems | 23-33 31 17 | Exhaust Hood Fire Suppression System | 13-57 13 13 | Kitchen Space
System | D4010.50 | Not on One-Line | D4010.50 - Fire Protection, Non-Water-Based - (System) Wet Chemical Extinguishing | D4010.50 - Fire Protection, Non-Water-Based | (System) Wet Chemical Extinguishing |  | D. Fire Protection, Non-Water-Based - (System) Wet Chemical Extinguishing | D. Fire Protection, Non-Water-Based | (System) Wet Chemical Extinguishing |  | SYS Wet Chemical Extinguishing ([Area Served]) | Each System | Track by location | Fire extinguishers of this type are available in hand portable models of 1-1/2 gal (6 L)/2 and 2 1/2 gal (9.46 L). The extinguishing agent can be comprised of, but is not limited to, solutions of water and potassium acetate, potassium carbonate, potassium citrate, or a combination of these chemicals (which are conductors of electricity). The liquid agent typically has a pH of 9.0 or less. On Class A fires, the agent works as a coolant. On Class K fires (cooking oil fires), the agent forms a foam blanket to prevent reignition. The water content of the agent aids in cooling and reducing the temperature of the hot oils and fats below their autoignition point. The agent, when discharged as a fine spray directly at cooking appliances, reduces the possibility of splashing hot grease and does not present a shock hazard to the operator. |  | 21-04 40 10 50 | Fire-Extinguishing | 22-21 23 00 | Wet-Chemical Fire-Extinguishing Systems | 23-29 33 13 17 | Wet Chemical Fire Suppression Equipment
Asset | D4010.50 | Not on One-Line | D4010.50 - Fire Protection, Non-Water-Based - Fire Extinguishers - Bottle | D4010.50 - Fire Protection, Non-Water-Based | Fire Extinguishers | Bottle | D. Fire Protection, Non-Water-Based - Fire Extinguishers - Bottle | D. Fire Protection, Non-Water-Based | Fire Extinguishers | Bottle | Fire Extinguishers - Bottle | Each fire extinguisher | On extinguisher bottle | A portable device, carried or on wheels and operated by hand, containing an extinguishing agent that can be expelled under pressure for the purpose of suppressing or extinguishing fire. |  | 21-04 40 10 50 | Fire-Extinguishing | 22-10 44 16 | Fire Extinguishers | 23-29 25 19 | Fire Extinguishers
Asset | D4010.50 | Not on One-Line | D4010.50 - Fire Protection, Non-Water-Based - Fire Extinguishers - Location | D4010.50 - Fire Protection, Non-Water-Based | Fire Extinguishers | Location | D. Fire Protection, Non-Water-Based - Fire Extinguishers - Location | D. Fire Protection, Non-Water-Based | Fire Extinguishers | Location | Fire Extinguishers - Location | Each fire extinguisher | On wall behind/above bracket | This is the location that the fire extinguisher - bottle is installed and the point of the monthly inspection. |  | 21-04 40 10 50 | Fire-Extinguishing | 22-21 20 00 | Fire-Extinguishing Systems | 23-29 25 19 | Fire Extinguishers
Supplemental Elements | D4010.50.99 | n/a | D4010.50 - Fire Protection, Non-Water-Based - [Supplemental Elements] Non-Water-Based Fire Suppression | D4010.50 - Fire Protection, Non-Water-Based | [Supplemental Elements] Non-Water-Based Fire Suppression |  | D. Fire Protection, Non-Water-Based - [Supplemental Elements] Non-Water-Based Fire Suppression | D. Fire Protection, Non-Water-Based | [Supplemental Elements] Non-Water-Based Fire Suppression |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D5010 |  | D5010 - Electrical Power Generation | D5010 - Electrical Power Generation |  |  | D. Electrical Power Generation | D. Electrical Power Generation | [5 empty] | General Category |  | 21-04 50 10 | Facility Power Generation
System | D5010 | D50-1 | D5010 - Electrical Power Generation - (System) Power Generation | D5010 - Electrical Power Generation | (System) Power Generation |  | D. Electrical Power Generation - (System) Power Generation | D. Electrical Power Generation | (System) Power Generation |  | SYS Power Generation ([Area Served]) | Each system | No barcode - Track by location | Generic representation of system. This is often tracked under Electrical Service and Distribution (Emergency) |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D5010.10 | D50-1 | D5010 - Electrical Power Generation - Emergency Power Generator | D5010 - Electrical Power Generation | Emergency Power Generator |  | D. Electrical Power Generation - Emergency Power Generator | D. Electrical Power Generation | Emergency Power Generator |  | Emergency Power Generator | Each generator, incl. battery and load bank | On control panel | Internal combustion engine driving AC generator to power hospital emergency circuits. |  | 21-04 50 10 10 | Packaged Generator Assemblies | 22-26 32 13 | Engine Generators | 23-35 11 00 | Electrical Generators
Asset | D5010.10 | D50-1 | D5010 - Electrical Power Generation - Emergency Power Generator - Diesel | D5010 - Electrical Power Generation | Emergency Power Generator | Diesel | D. Electrical Power Generation - Emergency Power Generator - Diesel | D. Electrical Power Generation | Emergency Power Generator | Diesel | Emergency Power Generator - Diesel | Each generator, incl. battery and load bank | On control panel | Diesel internal combustion engine driving AC generator to power hospital emergency circuits. |  | 21-04 50 10 10 | Packaged Generator Assemblies | 22-26 32 13 | Engine Generators | 23-35 11 00 | Electrical Generators
Asset | D5010.10 | D50-1 | D5010 - Electrical Power Generation - Emergency Power Generator - Natural Gas | D5010 - Electrical Power Generation | Emergency Power Generator | Natural Gas | D. Electrical Power Generation - Emergency Power Generator - Natural Gas | D. Electrical Power Generation | Emergency Power Generator | Natural Gas | Emergency Power Generator - Natural Gas | Each generator, incl. battery and load bank | On control panel | Natural gas combustion engine driving AC generator to power hospital emergency circuits. |  | 21-04 50 10 10 | Packaged Generator Assemblies | 22-26 32 13 | Engine Generators | 23-35 11 00 | Electrical Generators
Asset | D5010.10 | D50-1 | D5010 - Electrical Power Generation - Gas Powered Turbine | D5010 - Electrical Power Generation | Gas Powered Turbine |  | D. Electrical Power Generation - Gas Powered Turbine | D. Electrical Power Generation | Gas Powered Turbine |  | Gas Powered Turbine | Each Turbine | On control panel | This is a device that is used to produce electrical power and heat from a gas powered turbine. Normally found in a Cogen plant. |  | 21-04 50 10 90 | Facility Power Generation Supplementary Components | 22-26 32 13 26 | Gas-Turbine Engine-Driven Generators | 23-35 11 12 13 | Electrical Generation Gas Engines
Asset | D5010.10 | D50-1 | D5010 - Electrical Power Generation - Generator Radiator Fan | D5010 - Electrical Power Generation | Generator Radiator Fan |  | D. Electrical Power Generation - Generator Radiator Fan | D. Electrical Power Generation | Generator Radiator Fan |  | Generator Radiator Fan | Each Unit | On frame by nameplate. | A fan used to provide cooling to an emergency generator system. The radiator and fan are typical installed in a separate location such as a roof or alley and provided in areas where ventilation is not available to the generator room. |  | 21-04 50 10 90 | Facility Power Generation Supplementary Components | 22-26 32 00 | Packaged Generator Assemblies
Asset | D5010.20 | D50-1 | D5010 - Electrical Power Generation - Battery Rack | D5010 - Electrical Power Generation | Battery Rack |  | D. Electrical Power Generation - Battery Rack | D. Electrical Power Generation | Battery Rack |  | Battery Rack | Each rack - (Data Center Batteries; generator batteries to be tracked as component of generator) | On rack | Any frame work designed to support batteries used for engine starting. |  | 21-04 50 10 20 | Battery Equipment | 22-26 33 16 | Battery Racks | 23-35 19 11 | Battery Racks
Asset | D5010.20 | D50-1 | D5010 - Electrical Power Generation - Load Bank | D5010 - Electrical Power Generation | Load Bank |  | D. Electrical Power Generation - Load Bank | D. Electrical Power Generation | Load Bank |  | Load Bank | Each Unit | On frame by nameplate. | A load bank is a device which develops an electrical load, applies the load to an electrical power source and converts or dissipates the resultant power output of the source in the form of heat energy. |  | 21-04 50 10 90 | Facility Power Generation Supplementary Components | 22-33 71 26 13 | Capacitor Banks | 23-35 19 11 | Battery Racks
Asset | D5010.20 | Not on One-Line | D5010 - Electrical Power Generation - Uninterruptible Power Supply | D5010 - Electrical Power Generation | Uninterruptible Power Supply |  | D. Electrical Power Generation - Uninterruptible Power Supply | D. Electrical Power Generation | Uninterruptible Power Supply |  | Uninterruptible Power Supply | Each UPS unit | Inside cover | A power supply which includes battery packs, switch devices, etc., and is usually utilized in computer rooms to provide a steady power supply and to allow for an orderly shutdown of computer equipment and related components in the event of a power failure. |  | 21-04 50 10 20 | Battery Equipment | 22-26 33 00 |  | 23-35 23 21 | Uninterrupted Power Supply (UPS) Units
Asset | D5010.30 | Not on One-Line | D5010 - Electrical Power Generation - Photovoltaic Collectors | D5010 - Electrical Power Generation | Photovoltaic Collectors |  | D. Electrical Power Generation - Photovoltaic Collectors | D. Electrical Power Generation | Photovoltaic Collectors |  | Photovoltaic Collectors | Each system | Track by location | The panels that absorb the sun's energy and convert it to usable electrical power. |  | 21-04 50 10 30 | Photovoltaic Collectors | 22-26 31 00 | Photovoltaic Collectors | 23-35 11 17 15 | Photovoltaic Collectors
Asset | D5010.70 | D50-1 | D5010 - Electrical Power Generation - Automatic Transfer Switch | D5010 - Electrical Power Generation | Automatic Transfer Switch |  | D. Electrical Power Generation - Automatic Transfer Switch | D. Electrical Power Generation | Automatic Transfer Switch |  | Automatic Transfer Switch ([Area Served]) | Each ATS | Outside on unit, to right of transfer switch to right of nameplate or controls panel. | Automatic transfer switches used for automatically swapping power supply from one source (typically utility) to another (typically emergency source) and vice-versa. |  | 21-04 50 10 70 | Transfer Switches | 22-26 36 23 | Automatic Transfer Switches | 23-35 37 11 | Automatic Transfer Switches
Asset | D5010.70 | D50-1 | D5010 - Electrical Power Generation - Manual Transfer Switch | D5010 - Electrical Power Generation | Manual Transfer Switch |  | D. Electrical Power Generation - Manual Transfer Switch | D. Electrical Power Generation | Manual Transfer Switch |  | Manual Transfer Switch | Each TS | Outside on unit, to right of transfer switch to right of nameplate or controls panel. | Manual transfer switches used for manually swapping power supply from one source (typically utility) to another (typically emergency source) and vice-versa. |  | 21-04 50 10 70 | Transfer Switches | 22-26 36 00 |  | 23-35 37 13 | Manual Transfer Switches
Asset | D5010.90 | D50-1 | D5010 - Electrical Power Generation - Synchronizing Switchgear | D5010 - Electrical Power Generation | Synchronizing Switchgear |  | D. Electrical Power Generation - Synchronizing Switchgear | D. Electrical Power Generation | Synchronizing Switchgear |  | Synchronizing Switchgear | Each cabinet | On cover | Electrical equipment consisting of gear for paralleling generator to the electric network; usually packaged integrally with gensets. While it may be tagged separately as an asset, it should be assessed as an integral part of the generator unit. |  | 21-04 50 10 90 | Facility Power Generation Supplementary Components | 22-26 23 13 | Paralleling Low-Voltage Switchgear | 23-35 31 31 13 | Paralleling Switchgear
Supplemental Elements | D5010.99 | n/a | D5010 - Electrical Power Generation - [Supplemental Elements] Electrical Power Generation | D5010 - Electrical Power Generation | [Supplemental Elements] Electrical Power Generation |  | D. Electrical Power Generation - [Supplemental Elements] Electrical Power Generation | D. Electrical Power Generation | [Supplemental Elements] Electrical Power Generation |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D5020 |  | D5020 - Electrical Service and Distribution | D5020 - Electrical Service and Distribution |  |  | D. Electrical Service and Distribution | D. Electrical Service and Distribution | [5 empty] | General Category |  | 21-04 50 20 | Electrical Service and Distribution | 22-26 20 00 | Low-Voltage Electrical Transmission | 23-35 13 00 | Transformers
System | D5020.10 |  | D5020 - Electrical Service and Distribution - (System) Electrical Service and Distribution | D5020 - Electrical Service and Distribution | (System) Electrical Service and Distribution |  | D. Electrical Service and Distribution - (System) Electrical Service and Distribution | D. Electrical Service and Distribution | (System) Electrical Service and Distribution |  | SYS Electrical Service and Distribution ([Area Served]) | Each system | No barcode - Track by location | Generic representation of system |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | D5020.10 | D50-2 | D5020 - Electrical Service and Distribution - Electrical Sub Meter | D5020 - Electrical Service and Distribution | Electrical Sub Meter |  | D. Electrical Service and Distribution - Electrical Sub Meter | D. Electrical Service and Distribution | Electrical Sub Meter |  | Electrical Sub Meter | Each unit | On outside of panel | An electric meter utilized to measure consumption to tenants and often communicating to a central panel or web application. |  | 21-04 50 20 90 | Electrical Service and Distribution Supplementary Components | 22-26 16 00 | Medium-Voltage Metering | 23-35 25 11 | Electrical Meters
Asset | D5020.10 | D50-1 | D5020 - Electrical Service and Distribution - Switchboard | D5020 - Electrical Service and Distribution | Switchboard |  | D. Electrical Service and Distribution - Switchboard | D. Electrical Service and Distribution | Switchboard |  | Switchboard - [Source] | Each board | Outside on unit, to right of switchboard name/nameplate if present | Device that directs electricity from one or more sources of supply to several smaller regions of usage. It is an assembly of one or more panels, each of which contains switches that allow electricity to be redirected. Switchboards are normally located in an electrical closest and are used to distribute power to other types of electrical equipment such as lighting, Distribution Power Panels and Motor Control Centers. |  | 21-04 50 20 10 | Power Distribution | multiple | Switchgear | 23-35 31 29 | Switchboards
Asset | D5020.10 | D50-1 | D5020 - Electrical Service and Distribution - Switchgear | D5020 - Electrical Service and Distribution | Switchgear |  | D. Electrical Service and Distribution - Switchgear | D. Electrical Service and Distribution | Switchgear |  | Switchgear - [Source] | Each cabinet | On cover | Switchgear is composed of electrical disconnect switches, fuses or circuit breakers used to control, protect and isolate electrical equipment. Switchgear is used both to de-energize equipment to allow work to be done and to clear faults downstream. A switchgear differentiates itself from a switchboard as it contains control relays, meters and other devices and are normally found in the location of a building where power is supplied from the local utility. Switchgear can be part of a substation that includes transformers, high voltage switches and tie breakers. |  | 21-04 50 20 10 | Power Distribution | 22-26 24 13 | Switchboards | 23-35 31 29 | Switchboards
Asset | D5020.10 | D50-2 | D5020 - Electrical Service and Distribution - Transformer - Dry | D5020 - Electrical Service and Distribution | Transformer | Dry | D. Electrical Service and Distribution - Transformer - Dry | D. Electrical Service and Distribution | Transformer | Dry | Transformer - Dry - [Source] | Each transformer | On nameplate | A voltage rising or lowering device with dry insulating material. These are usually used to supply 480, 240, and120 volts for outlets within a building when a higher voltage is used for most other building loads such as lighting and equipment. |  | 21-04 50 20 30 | Power Distribution | 22-26 12 16 | Dry-Type, Medium-Voltage Transformers | 23-35 13 17 15 11 | Power Dry Step Down Transformers
Asset | D5020.10 | D50-2 | D5020 - Electrical Service and Distribution - Transformer - Oil | D5020 - Electrical Service and Distribution | Transformer | Oil | D. Electrical Service and Distribution - Transformer - Oil | D. Electrical Service and Distribution | Transformer | Oil | Transformer - Oil - [Source] | Each transformer | On nameplate | A large electrical power transformer used for dropping primary voltage to secondary voltage. Transformer cavity filled with oil for insulating and cooling purposes. |  | 21-04 50 20 30 | Power Distribution | 22-26 12 13 | Liquid-Filled, Medium-Voltage Transformers | 23-35 13 17 15 13 | Power Oil Filled Step Down Transformers
Asset | D5020.10 | Not on One-Line | D5020 - Electrical Service and Distribution - Transformer - Type not specified | D5020 - Electrical Service and Distribution | Transformer | Type not specified | D. Electrical Service and Distribution - Transformer - Type not specified | D. Electrical Service and Distribution | Transformer | Type not specified | Transformer - [Specify Type] - [Source] | Each transformer | On nameplate | An electric device consisting essentially of two or more windings wound on the same core, which by electromagnetic induction transforms electric energy from one set of one or more circuits to another set of one or more circuits such that the frequency of the energy remains unchanged while the voltage and current usually change. |  | 21-04 50 20 30 | Power Distribution | 22-26 12 00 | Medium-Voltage Transformers | 23-35 13 17 | Power Transformers
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Bus Duct | D5020 - Electrical Service and Distribution | Bus Duct |  | D. Electrical Service and Distribution - Bus Duct | D. Electrical Service and Distribution | Bus Duct |  | Bus Duct - [Source] | Each Circuit | At point leaving distribution panel. | A bus duct is a sheet metal duct containing either copper or aluminum busbars for the purpose of conducting a substantial current of electricity. It is an alternative means of conducting electricity to power cables or cable bus. |  | 21-04 50 20 30 | Power Distribution | 22-26 25 00 | Enclosed Bus Assemblies | 23-35 31 33 | Electrical Busbars
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Bus Duct Switch | D5020 - Electrical Service and Distribution | Bus Duct Switch |  | D. Electrical Service and Distribution - Bus Duct Switch | D. Electrical Service and Distribution | Bus Duct Switch |  | Bus Duct Switch - [Source] | Each Unit | On front of cover by nameplate. | A bus duct switch is a type of disconnection switch that is specially designed to be easily mounted and dismounted from a bus duct. |  | 21-04 50 20 30 | Power Distribution | 22-26 25 00 | Enclosed Bus Assemblies | 23-35 37 00 | Electrical Switches
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Circuit Breaker | D5020 - Electrical Service and Distribution | Circuit Breaker |  | D. Electrical Service and Distribution - Circuit Breaker | D. Electrical Service and Distribution | Circuit Breaker |  | Circuit Breaker | Typically not tracked separately | n/a | Molded case circuit breakers are a type of electrical protection device that is commonly used when load currents exceed the capabilities of miniature circuit breakers. They are also used in applications of any current rating that require adjustable trip settings, which are not available in plug-in circuit breakers and MCBs. |  | 21-04 50 20 30 | Power Distribution | 22-26 28 16 13 | Enclosed Circuit Breakers | 23-35 29 00 | Circuit Breakers
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Circuit Breaker - Molded Case | D5020 - Electrical Service and Distribution | Circuit Breaker | Molded Case | D. Electrical Service and Distribution - Circuit Breaker - Molded Case | D. Electrical Service and Distribution | Circuit Breaker | Molded Case | Circuit Breaker - Molded Case | Typically not tracked separately | n/a | A non-molded case circuit breaker is typically a large breaker, contained in the switchgear cabinet. |  | 21-04 50 20 30 | Power Distribution | 22-26 28 16 13 | Enclosed Circuit Breakers | 23-35 29 00 | Circuit Breakers
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Disconnect Switch | D5020 - Electrical Service and Distribution | Disconnect Switch |  | D. Electrical Service and Distribution - Disconnect Switch | D. Electrical Service and Distribution | Disconnect Switch |  | Disconnect Switch | Typically tracked as part of main device | On cover (if barcoded) | An unfused disconnect switch at the power entry point or a piece of equipment to power it on and off. |  | 21-04 50 20 30 | Power Distribution | 22-26 28 16 16 | Enclosed Switches | 23-35 37 19 | Disconnect Switches
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Disconnect Switch Fused | D5020 - Electrical Service and Distribution | Disconnect Switch Fused |  | D. Electrical Service and Distribution - Disconnect Switch Fused | D. Electrical Service and Distribution | Disconnect Switch Fused |  | Disconnect Switch Fused | Typically tracked as part of main device | On cover (if barcoded) | A fused disconnect switch at the power entry point or a piece of equipment to power it on and off. |  | 21-04 50 20 30 | Power Distribution | 22-26 28 16 16 | Enclosed Switches | 23-35 37 19 11 | Fused Disconnect Switches
Asset | D5020.30 | D50-1 | D5020 - Electrical Service and Distribution - Fuse Box | D5020 - Electrical Service and Distribution | Fuse Box |  | D. Electrical Service and Distribution - Fuse Box | D. Electrical Service and Distribution | Fuse Box |  | Fuse Box | Only used in old facilities. Should best be tracked with downstream asset (unless fuse box feeds multiple assets) | On cover (if barcoded) | An electrical fuse box utilizes thermal element to interrupt electrical feeder circuits in the event of a current overload. Most systems built before 1960 will have a fuse box, those built after have a circuit breakers in a Distribution Power Panel. |  | 21-04 50 20 30 | Power Distribution | 22-26 28 13 | Fuses | 23-35 29 29 | Fuses
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Line Isolation Monitor | D5020 - Electrical Service and Distribution | Line Isolation Monitor |  | D. Electrical Service and Distribution - Line Isolation Monitor | D. Electrical Service and Distribution | Line Isolation Monitor |  | Line Isolation Monitor - [Source] | Each MCC | By nameplate | Panel with multiple contactors or circuit breakers in buckets, each controlling a motor that drives equipment. MCCs serving a single, associated asset should be consolidated to that downstream asset. |  | 21-04 50 20 30 | Power Distribution | 22-26 24 19 | Motor-Control Centers | 23-35 31 23 | Motor Control Centers
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Motor Control Center | D5020 - Electrical Service and Distribution | Motor Control Center |  | D. Electrical Service and Distribution - Motor Control Center | D. Electrical Service and Distribution | Motor Control Center |  | Motor Control Center - [Source] | Each Motor Controller | On MCC compartment | A circuit breaker or contactor used to control electrical power to a large single electrical load such as a motor or heater bank. Typically this is tracked as part of the controlled asset and associated with a stand alone driven motor to drive an individual piece of equipment (distinguish from motor control center which houses controllers for multiple motors). |  | 21-04 50 20 30 | Power Distribution | 22-26 29 13 | Enclosed Controllers | 23-35 15 00 | Electric Motors
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Motor Controller | D5020 - Electrical Service and Distribution | Motor Controller |  | D. Electrical Service and Distribution - Motor Controller | D. Electrical Service and Distribution | Motor Controller |  | Motor Controller - [Source] | Generic asset representing outlets | By area | Typically, power receptacles for 120 volt AC 15 to 20 amps accessible to the general public. Can also be for other voltages and high amperage. |  | 21-04 50 20 30 | Power Distribution | 22-26 27 00 | Low-Voltage Distribution Equipment | 23-35 27 11 | Electrical Receptacles
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Outlets | D5020 - Electrical Service and Distribution | Outlets |  | D. Electrical Service and Distribution - Outlets | D. Electrical Service and Distribution | Outlets |  | Outlet - [Source] | Each panel | On outside of panel, to right of panel name/nameplate if present | The final distribution point to individual circuits. |  | 21-04 50 20 30 | Power Distribution | 22-26 24 16 | Panelboards | 23-35 31 17 | Electrical Panel Boards
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Panel, Branch | D5020 - Electrical Service and Distribution | Panel, Branch |  | D. Electrical Service and Distribution - Panel, Branch | D. Electrical Service and Distribution | Panel, Branch |  | Panel, Branch - [Source] | Each panel | On outside of panel, to right of panel name/nameplate if present | A FCO is a protective circuit that is dedicated to a fire alarm system. It often is found taking power right from the service entrance panel. |  | 21-04 50 20 30 | Power Distribution | 22-26 24 16 | Panelboards | 23-35 29 29 11 | Fuse Panels
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Panel, Fused Cutout | D5020 - Electrical Service and Distribution | Panel, Fused Cutout |  | D. Electrical Service and Distribution - Panel, Fused Cutout | D. Electrical Service and Distribution | Panel, Fused Cutout |  | Panel, Fused Cutout - Emergency | Each line isolation monitor | On outside of panel, to right of panel name/nameplate if present | A isolation indicating monitor, which may be remote or integral to the Isolated power panel. |  | 21-04 50 20 30 | Power Distribution | 22-26 24 16 | Panelboards | 23-35 31 15 | Electrical Distribution Control Panels
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Panel, Power Distribution | D5020 - Electrical Service and Distribution | Panel, Power Distribution |  | D. Electrical Service and Distribution - Panel, Power Distribution | D. Electrical Service and Distribution | Panel, Power Distribution |  | Panel, Power Distribution - [Source] | Each panel | On outside of panel, to right of panel name/nameplate if present | These panels distribute power to subsidiary circuits or equipment, and are equipped with a main line breaker for the supply feed as well as a number of breakers feeding individual equipment/supply circuits. Note that the distinguishing characteristic of this category is that this equipment is associated with larger equipment drives and significant subsidiary circuits, as compared, for example, to panels that feed lighting circuits and minor equipment. |  | 21-04 50 20 30 | Power Distribution | 22-26 24 16 | Panelboards | 23-35 31 13 | Distribution Panel Boards
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Power Filtering and Conditioning | D5020 - Electrical Service and Distribution | Power Filtering and Conditioning |  | D. Electrical Service and Distribution - Power Filtering and Conditioning | D. Electrical Service and Distribution | Power Filtering and Conditioning |  | Power Filtering and Conditioning | Each unit | On control panel | Electrical capacitors, reactors, and resistive elements that vary depending upon use/purpose. Examples are to modulate reactive power, mitigate current harmonics or protect against surges. |  | 21-04 50 20 30 | Power Distribution | 22-26 35 00 | Power Filters and Conditioners | 23-35 23 00 | Power Conditioning Equipment
Asset | D5020.30 | D50-2 | D5020 - Electrical Service and Distribution - Variable Frequency Drive | D5020 - Electrical Service and Distribution | Variable Frequency Drive |  | D. Electrical Service and Distribution - Variable Frequency Drive | D. Electrical Service and Distribution | Variable Frequency Drive |  | Variable Frequency Drive | Each VFD (linked to equipment it serves) | Outside of VFD on front cover | Adjustable-speed drive used to control AC motor speed and torque by varying motor input frequency and voltage. These devices should be condition assessed as part of underlying driven equipment. |  | 21-04 50 20 30 | Power Distribution | 22-26 29 23 | Variable-Frequency Motor Controllers | 23-35 17 15 | Variable Frequency Drives
Supplemental Elements | D5020.99 | n/a | D5020 - Electrical Service and Distribution - [Supplemental Elements] Electrical Service and Distribution | D5020 - Electrical Service and Distribution | [Supplemental Elements] Electrical Service and Distribution |  | D. Electrical Service and Distribution - [Supplemental Elements] Electrical Service and Distribution | D. Electrical Service and Distribution | [Supplemental Elements] Electrical Service and Distribution |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D5040.10 |  | D5040.10 - Electrical Lighting Control | D5040.10 - Electrical Lighting Control |  |  | D. Electrical Lighting Control | D. Electrical Lighting Control | [5 empty] | General Category |  | 21-04 50 40 | Lighting | 22-26 09 23 | Lighting Control Devices
Asset | D5040.10 | D50-2c | D5040.10 - Electrical Lighting Control - Lighting Control Panel | D5040.10 - Electrical Lighting Control | Lighting Control Panel |  | D. Electrical Lighting Control - Lighting Control Panel | D. Electrical Lighting Control | Lighting Control Panel |  | Lighting Control Panel | Each panel | On outside of panel, to right of panel name/nameplate if present | Utilized to control lighting circuits. Commonly has dimming and programmable functions. |  | 21-04 50 40 10 | Lighting Control | 22-26 09 26 | Lighting Control Panelboards | 23-35 31 17 | Electrical Panel Boards
Grouping | D5040.50 |  | D5040.50 - Electrical Lighting Fixtures | D5040.50 - Electrical Lighting Fixtures |  |  | D. Electrical Lighting Fixtures | D. Electrical Lighting Fixtures | [5 empty] | General Category |  | 21-04 50 40 50 | Lighting Fixtures | 22-26 50 00 |  | 23-35 47 11 | Lighting Fixtures
System | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - (System) Emergency Lighting | D5040.50 - Electrical Lighting Fixtures | (System) Emergency Lighting |  | D. Electrical Lighting Fixtures - (System) Emergency Lighting | D. Electrical Lighting Fixtures | (System) Emergency Lighting |  | SYS Emergency Lighting ([Area Served]) | As needed | Track by area served | A hard wired traditional phone system such as a private branch exchange. |  | 21-04 60 20 20 | Voice Communications Terminal Equipment | 22-27 32 43 | Radio Communications Equipment | 23-37 23 13 | Telephones
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Egress Light - Battery | D5040.50 - Electrical Lighting Fixtures | Egress Light | Battery | D. Electrical Lighting Fixtures - Egress Light - Battery | D. Electrical Lighting Fixtures | Egress Light | Battery | Egress Light - Battery | Each fixture | On fixture | This a device used to provide lighting along an egress path in the event of an emergency. This device is backed up by a battery. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 52 00 | Emergency Lighting | 23-35 47 11 20 | Security Lighting Fixtures
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Egress Light - Power source to be specified | D5040.50 - Electrical Lighting Fixtures | Egress Light | Power source to be specified | D. Electrical Lighting Fixtures - Egress Light - Power source to be specified | D. Electrical Lighting Fixtures | Egress Light | Power source to be specified | Egress Light - [Battery or Wired] | Each fixture | On fixture | This a device used to provide lighting along an egress path in the event of an emergency. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 52 00 | Emergency Lighting | 23-35 47 11 20 | Security Lighting Fixtures
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Egress Light - Wired | D5040.50 - Electrical Lighting Fixtures | Egress Light | Wired | D. Electrical Lighting Fixtures - Egress Light - Wired | D. Electrical Lighting Fixtures | Egress Light | Wired | Egress Light - Wired | Each fixture | On fixture | An exit sign is a device in a public facility (such as a building, aircraft, or boat) denoting the location of the closest emergency exit in case of fire or other emergency. Most relevant codes (fire, building, health, or safety) require exit signs to be permanently lit. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 52 00 | Emergency Lighting | 23-35 47 11 20 | Security Lighting Fixtures
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Exit Sign - Battery | D5040.50 - Electrical Lighting Fixtures | Exit Sign | Battery | D. Electrical Lighting Fixtures - Exit Sign - Battery | D. Electrical Lighting Fixtures | Exit Sign | Battery | Exit Sign - Battery | Each fixture | On fixture, on right side of surface mounted, and bottom right under "T" for non-box type exit sign | An exit sign, battery is a device in a public facility denoting the location of the closest emergency exit in case of fire or other emergency. This version of the exit sign is backed up by an internal battery. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 53 00 | Exit Signs | 23-35 47 15 11 | Battery Backup Exit Illuminated Signs
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Exit Sign - Power source to be specified | D5040.50 - Electrical Lighting Fixtures | Exit Sign | Power source to be specified | D. Electrical Lighting Fixtures - Exit Sign - Power source to be specified | D. Electrical Lighting Fixtures | Exit Sign | Power source to be specified | Exit Sign - [Battery or Wired] | Each fixture | On fixture, on right side of surface mounted, and bottom right under "T" for non-box type exit sign | An exit sign, battery is a device in a public facility denoting the location of the closest emergency exit in case of fire or other emergency. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 53 00 | Exit Signs | 23-35 47 15 11 | Battery Backup Exit Illuminated Signs
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Exit Sign - Wired | D5040.50 - Electrical Lighting Fixtures | Exit Sign | Wired | D. Electrical Lighting Fixtures - Exit Sign - Wired | D. Electrical Lighting Fixtures | Exit Sign | Wired | Exit Sign - Wired | Each fixture | On fixture, on right side of surface mounted, and bottom right under "T" for non-box type exit sign | An exit sign, wired is a device in a public facility denoting the location of the closest emergency exit in case of fire or other emergency. This version of the exit sign is permanently wired to a life safety power source. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 53 00 | Exit Signs | 23-35 47 15 13 | Hard Wired Backup Exit Illuminated Signs
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Exit Sign and Egress Light Combo - Battery | D5040.50 - Electrical Lighting Fixtures | Exit Sign and Egress Light Combo | Battery | D. Electrical Lighting Fixtures - Exit Sign and Egress Light Combo - Battery | D. Electrical Lighting Fixtures | Exit Sign and Egress Light Combo | Battery | Exit Sign and Egress Light Combo - Battery | Each fixture | On fixture | This is an exit sign with an egress light backed up by an internal battery. These exit sign/egress light combos are typically found in egress pathways. An exit sign is a device in a public facility denoting the location of the closest emergency exit in case of fire or other emergency. By code, these signs must be permanently lit and visible. Exit signs without batteries are normally connected to an emergency power source. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 53 00 | Exit Signs | 23-35 47 15 11 | Battery Backup Exit Illuminated Signs
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Exit Sign and Egress Light Combo - Power source to be specified | D5040.50 - Electrical Lighting Fixtures | Exit Sign and Egress Light Combo | Power source to be specified | D. Electrical Lighting Fixtures - Exit Sign and Egress Light Combo - Power source to be specified | D. Electrical Lighting Fixtures | Exit Sign and Egress Light Combo | Power source to be specified | Exit Sign and Egress Light Combo - [Battery or Wired] | Each fixture | On fixture | This is an exit sign with an egress light backed up by an internal battery. These exit sign/egress light combos are typically found in egress pathways. An exit sign is a device in a public facility denoting the location of the closest emergency exit in case of fire or other emergency. By code, these signs must be permanently lit and visible. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 53 00 | Exit Signs | 23-35 47 15 11 | Battery Backup Exit Illuminated Signs
Asset | D5040.50 | D50-3 | D5040.50 - Electrical Lighting Fixtures - Exit Sign and Egress Light Combo - Wired | D5040.50 - Electrical Lighting Fixtures | Exit Sign and Egress Light Combo | Wired | D. Electrical Lighting Fixtures - Exit Sign and Egress Light Combo - Wired | D. Electrical Lighting Fixtures | Exit Sign and Egress Light Combo | Wired | Exit Sign and Egress Light Combo - Wired | Each fixture | On fixture | This is an exit sign with an egress light backed up by an internal battery. These exit sign/egress light combos are typically found in egress pathways. An exit sign is a device in a public facility denoting the location of the closest emergency exit in case of fire or other emergency. By code, these signs must be permanently lit and visible. Exit signs without batteries are normally connected to an emergency power source. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 53 00 | Exit Signs | 23-35 47 15 11 | Battery Backup Exit Illuminated Signs
Asset | D5040.50 | Not on One-Line | D5040.50 - Electrical Lighting Fixtures - Surgical Light | D5040.50 - Electrical Lighting Fixtures | Surgical Light |  | D. Electrical Lighting Fixtures - Surgical Light | D. Electrical Lighting Fixtures | Surgical Light |  | Surgical Light | Each fixture | On fixture | A high intensity light fixture with multiple elements, typically in a surgical suite, that can be mounted to a wall/ceiling or roll around. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 55 70 | Healthcare Lighting | 23-25 59 13 17 11 | Surgical Operating Room Lighting Fixtures
Asset | D5040.50 | Not on One-Line | D5040.50 - Electrical Lighting Fixtures - Task Light, Battery | D5040.50 - Electrical Lighting Fixtures | Task Light, Battery |  | D. Electrical Lighting Fixtures - Task Light, Battery | D. Electrical Lighting Fixtures | Task Light, Battery |  | Task Light, Battery | Each fixture | On fixture | This is a battery powered task light that is normally installed in operating rooms and emergency generator rooms/enclosures to allow personnel to perform a task in the event of a power failure. These lights are different then egress lighting which is used to illuminate an egress path in the case of a power failure. |  | 21-04 50 40 90 | Lighting Supplementary Components | 22-26 51 13 | Interior Lighting Fixtures, Lamps, And Ballasts | 23-35 47 11 21 | Specialized Lighting Fixtures
Supplemental Elements | D5040.50.99 | n/a | D5040.50 - Electrical Lighting Fixtures - [Supplemental Elements] Electrical Lighting | D5040.50 - Electrical Lighting Fixtures | [Supplemental Elements] Electrical Lighting |  | D. Electrical Lighting Fixtures - [Supplemental Elements] Electrical Lighting | D. Electrical Lighting Fixtures | [Supplemental Elements] Electrical Lighting |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D6020.20a |  | D6020.20 - Communications - Radio | D6020.20 - Communications - Radio |  |  | D. Communications - Radio | D. Communications - Radio | [5 empty] | General Category |  | 21-04 60 20 20 | Voice Communications Terminal Equipment | 22-27 32 43 | Radio Communications Equipment | 23-37 23 00 | Telecommunications Equipment
System | D6020.20a | Not on One-Line | D6020.20 - Communications - Radio - (System) Radio | D6020.20 - Communications - Radio | (System) Radio |  | D. Communications - Radio - (System) Radio | D. Communications - Radio | (System) Radio |  | SYS Radio | As needed | Track by area served | A hard wired traditional phone system such as a private branch exchange. |  | 21-04 60 20 20 | Voice Communications Terminal Equipment | 22-27 32 43 | Radio Communications Equipment | 23-37 23 13 | Telephones
Supplemental Elements | D6020.20a.99 | n/a | D6020.20 - Communications - Radio - [Supplemental Elements] Radio | D6020.20 - Communications - Radio | [Supplemental Elements] Radio |  | D. Communications - Radio - [Supplemental Elements] Radio | D. Communications - Radio | [Supplemental Elements] Radio |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D6020.20b |  | D6020.20 - Communications - Telephone | D6020.20 - Communications - Telephone |  |  | D. Communications - Telephone | D. Communications - Telephone | [5 empty] | General Category |  | 21-04 60 20 | Voice Communications | 22-27 30 00 | Voice Communications | 23-37 23 21 | Radio Communication Equipment
System | D6020.20b | Not on One-Line | D6020.20 - Communications - Telephone - (System) Telephone | D6020.20 - Communications - Telephone | (System) Telephone |  | D. Communications - Telephone - (System) Telephone | D. Communications - Telephone | (System) Telephone |  | SYS Telephone ([Area Served]) | As needed | Track by area served | Typically a two way communication system independent from wireless networks and owned and maintained privately. Utilizes "walkie-talkies" as the interface. Common for interplant general communication. |  | 21-04 60 20 20 | Voice Communications Terminal Equipment | 22-27 32 00 | Voice Communications Terminal Equipment | 23-37 23 21 15 | Wireless Radio Communication Equipment
Supplemental Elements | D6020.20b.99 | n/a | D6020.20 - Communications - Telephone - [Supplemental Elements] Telephone | D6020.20 - Communications - Telephone | [Supplemental Elements] Telephone |  | D. Communications - Telephone - [Supplemental Elements] Telephone | D. Communications - Telephone | [Supplemental Elements] Telephone |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D6030.10 |  | D6030.20 - Communications - Audio | D6030.20 - Communications - Audio |  |  | D. Communications - Audio | D. Communications - Audio | [5 empty] | General Category |  | 21-04 60 20 30 | Voice Communications Messaging | 22-27 33 00 | Voice Communications Messaging | 23-37 27 15 | Intercoms
System | D6030.10 | Not on One-Line | D6030.20 - Communications - Audio - (System) Audio | D6030.20 - Communications - Audio | (System) Audio |  | D. Communications - Audio - (System) Audio | D. Communications - Audio | (System) Audio |  | SYS Audio ([Area Served]) | Each system | Track by area served | This is a communication system that is used to broadcast messages via voice and speakers to a specific area or throughout. It is also commonly used for paging. |  | 21-04 60 20 30 | Voice Communications Messaging | 22-27 33 00 | Voice Communications Messaging | 23-37 27 15 11 | Audio Intercoms
Supplemental Elements | D6030.10.99 | n/a | D6030.20 - Communications - Audio - [Supplemental Elements] Audio | D6030.20 - Communications - Audio | [Supplemental Elements] Audio |  | D. Communications - Audio - [Supplemental Elements] Audio | D. Communications - Audio | [Supplemental Elements] Audio |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D6060.30a |  | D6060.30 - Communications - Nurse Call | D6060.30 - Communications - Nurse Call |  |  | D. Communications - Nurse Call | D. Communications - Nurse Call | [5 empty] | General Category |  | 21-04 60 60 30 | Healthcare Communications and Monitoring | 22-27 51 13 13 | Overhead Paging Systems | 23-37 27 13 11 | Emergency Notification Devices
System | D6060.30a | Not on One-Line | D6060.30 - Communications - Nurse Call - (System) Nurse Call | D6060.30 - Communications - Nurse Call | (System) Nurse Call |  | D. Communications - Nurse Call - (System) Nurse Call | D. Communications - Nurse Call | (System) Nurse Call |  | SYS Nurse Call ([Area Served]) | Each system | Track by area served | A hard wired annunciation system with call buttons accessible by patients that when activated will provide audible and visual indication at a nurses station. May also include wireless patient tracking capabilities. |  | 21-04 60 60 30 | Healthcare Communications and Monitoring | 22-27 51 23 70 | Healthcare Intercommunications and Program Systems | 23-37 27 17 13 | Nurse Call Equipment
Supplemental Elements | D6060.30a.99 | n/a | D6060.30 - Communications - Nurse Call - [Supplemental Elements] Audio | D6060.30 - Communications - Nurse Call | [Supplemental Elements] Audio |  | D. Communications - Audio - [Supplemental Elements] Audio | D. Communications - Audio | [Supplemental Elements] Audio |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D6060.30b |  | D6060.30 - Communications - Remote Telemetry Location System | D6060.30 - Communications - RTLS |  |  | D. Communications - RTLS | D. Communications - RTLS | [5 empty] | General Category |  | 21-04 60 60 30 | Healthcare Communications and Monitoring | 22-27 51 13 13 | Overhead Paging Systems | 23-37 27 13 11 | Emergency Notification Devices
System | D6060.30b | Not on One-Line | D6060.30 - Communications - RTLS - (System) Remote Telemetry Location System | D6060.30 - Communications - RTLS | (System) Remote Telemetry Location System |  | D. Communications - RTLS - (System) Remote Telemetry Location System | D. Communications - RTLS | (System) Remote Telemetry Location System |  | SYS Remote Telemetry Location System ([Area Served]) | Each system | Track by area served | A hard wired annunciation system with call buttons accessible by patients that when activated will provide audible and visual indication at a nurses station. May also include wireless patient tracking capabilities. |  | 21-04 60 60 30 | Healthcare Communications and Monitoring | 22-27 51 23 70 | Healthcare Intercommunications and Program Systems | 23-37 27 17 13 | Nurse Call Equipment
Supplemental Elements | D6060.30b.99 | n/a | D6060.30 - Communications - RTLS - [Supplemental Elements] Remote Telemetry Location System | D6060.30 - Communications - RTLS | [Supplemental Elements] Remote Telemetry Location System |  | D. Communications - RTLS - [Supplemental Elements] Remote Telemetry Location System | D. Communications - RTLS | [Supplemental Elements] Remote Telemetry Location System |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D6060.50 |  | D6060.50 - Communications - Clock System | D6060.50 - Communications - Clock System |  |  | D. Communications - Clock System | D. Communications - Clock System | [5 empty] | General Category |  | 21-04 60 | Communications | 22-27 53 13 | Clock Systems
System | D6060.50 | Not on One-Line | D6060.50 - Communications - Clock System - (System) Clock | D6060.50 - Communications - Clock System | (System) Clock |  | D. Communications - Clock System - (System) Clock | D. Communications - Clock System | (System) Clock |  | SYS Clock | Each clock | On fixture | Central clock systems are utilized less than in previous times but are still found. A central unit supplies a controlling signal to remote clocks installed throughout a building. Also, the system may consist of a few clocks, possibly wireless often installed in operating rooms. |  | 21-04 60 90 | Communications Supplementary Components | 22-27 53 13 | Clock Systems | 23-27 15 11 | Building Clock Controls
Supplemental Elements | D6060.50.99 | n/a | D6060.50 - Communications - Clock System - [Supplemental Elements] Clock | D6060.50 - Communications - Clock System | [Supplemental Elements] Clock |  | D. Communications - Clock System - [Supplemental Elements] Clock | D. Communications - Clock System | [Supplemental Elements] Clock |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D7010 |  | D7010 - Safety and Security | D7010 - Safety and Security |  |  | D. Safety and Security | D. Safety and Security | [5 empty] | General Category
System | D7010 | n/a | D7010 - Safety and Security - (System) Access Control and Surveillance | D7010 - Safety and Security | (System) Access Control and Surveillance |  | D. Safety and Security - (System) Access Control and Surveillance | D. Safety and Security | (System) Access Control and Surveillance |  | SYS Access Control and Surveillance ([Area Served]) | Each system | Track by area served | Access Control and Surveillance Systems
Supplemental Elements | D7010.99 | n/a | D7010 - Safety and Security - [Supplemental Elements] Access Control and Surveillance | D7010 - Safety and Security | [Supplemental Elements] Access Control and Surveillance |  | D. Safety and Security - [Supplemental Elements] Access Control and Surveillance | D. Safety and Security | [Supplemental Elements] Access Control and Surveillance |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D7050.10 |  | D7050.10 - Detection and Alarm - Fire Protection | D7050.10 - Detection and Alarm - Fire Protection |  |  | D. Detection and Alarm - Fire Protection | D. Detection and Alarm - Fire Protection | [5 empty] | General Category |  | 21-04 70 50 | Detection and Alarm | 22-28 31 00 | Fire Detection and Alarm
System | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - (System) Fire Alarm | D7050.10 - Detection and Alarm - Fire Protection | (System) Fire Alarm |  | D. Detection and Alarm - Fire Protection - (System) Fire Alarm | D. Detection and Alarm - Fire Protection | (System) Fire Alarm |  | SYS Fire Alarm ([Area Served]) | Generic asset for Fire Alarm System | Track by area served | A system or portion of a combination system that consists of components and circuits arranged to monitor and annunciate the status of fire alarm or supervisory signal-initiating devices and to initiate the appropriate response to those signals. (SIG-FUN) |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 11 | Digital, Addressable Fire-Alarm Systems | 23-29 31 23 | Fire Alarm Central Stations
Asset | D7050.10 | D40-1 | D7050.10 - Detection and Alarm - Fire Protection - Alarm Valve | D7050.10 - Detection and Alarm - Fire Protection | Alarm Valve |  | D. Detection and Alarm - Fire Protection - Alarm Valve | D. Detection and Alarm - Fire Protection | Alarm Valve |  | Alarm Valve | Each unit | On unit | An alarm valve prevents a reverse flow of water from the installation back to the supply, but in case a fire-sprinkler is activated (opened) due to fire, the alarm valve will open and permit water to flow into the system transmitting an alarm. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 | Fire Detection and Alarm Interfaces | 23-29 31 15 | Audible Fire Notification Devices
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Bell Audible Device | D7050.10 - Detection and Alarm - Fire Protection | Bell Audible Device |  | D. Detection and Alarm - Fire Protection - Bell Audible Device | D. Detection and Alarm - Fire Protection | Bell Audible Device |  | Bell Audible Device | Each unit | On unit | This is a notification appliance which the NFPA defines as “a fire alarm system component such as a bell, horn, speaker, light, or text display that provides audible, tactile, or visible outputs, or any combination thereof.” |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 63 13 | Fire Alarm Horns and Strobes | 23-29 31 15 11 | Audible Fire Notification Devices Bell
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Chime Audible Device | D7050.10 - Detection and Alarm - Fire Protection | Chime Audible Device |  | D. Detection and Alarm - Fire Protection - Chime Audible Device | D. Detection and Alarm - Fire Protection | Chime Audible Device |  | Chime Audible Device | Each unit | On unit | This is a notification appliance which the NFPA defines as “a fire alarm system component such as a bell, horn, speaker, light, or text display that provides audible, tactile, or visible outputs, or any combination thereof.” |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 63 13 | Fire Alarm Horns and Strobes | 23-29 31 15 15 | Audible Fire Notification Devices Chime
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Detector, Duct | D7050.10 - Detection and Alarm - Fire Protection | Detector, Duct |  | D. Detection and Alarm - Fire Protection - Detector, Duct | D. Detection and Alarm - Fire Protection | Detector, Duct |  | Detector, Duct | Each detector | On unit | Same as a smoke detector but installed in the discharge of a fan to shut the fan down when a smoke condition exists. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 43 | Fire Detection Sensors | 23-29 29 00 | Fire Detection Devices
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Detector, Fire-Gas (CO) | D7050.10 - Detection and Alarm - Fire Protection | Detector, Fire-Gas (CO) |  | D. Detection and Alarm - Fire Protection - Detector, Fire-Gas (CO) | D. Detection and Alarm - Fire Protection | Detector, Fire-Gas (CO) |  | Detector, Fire-Gas (CO) | Each detector | On unit | A device that detects gases produced by a fire. (SIG-IDS) |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 49 | Carbon-Monoxide Detection Sensors | 23-29 29 00 | Fire Detection Devices
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Detector, Heat | D7050.10 - Detection and Alarm - Fire Protection | Detector, Heat |  | D. Detection and Alarm - Fire Protection - Detector, Heat | D. Detection and Alarm - Fire Protection | Detector, Heat |  | Detector, Heat | Each detector | On unit | A fire detector that detects either abnormally high temperature or rate of temperature rise, or both. (SIG-IDS) |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 43 | Fire Detection Sensors | 23-29 29 13 13 | Heat Detectors
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Detector, Radiant Energy | D7050.10 - Detection and Alarm - Fire Protection | Detector, Radiant Energy |  | D. Detection and Alarm - Fire Protection - Detector, Radiant Energy | D. Detection and Alarm - Fire Protection | Detector, Radiant Energy |  | Detector, Radiant Energy | Each unit | On unit | A radiant energy–sensing fire detector connected to a fire alarm system that is designed to detect sparks or embers, or both. These devices are normally intended to operate in dark environments and in the infrared part of the spectrum. (SIG-IDS) |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 43 | Fire Detection Sensors | 23-29 29 13 19 | Radiant Energy Detectors
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Detector, Smoke | D7050.10 - Detection and Alarm - Fire Protection | Detector, Smoke |  | D. Detection and Alarm - Fire Protection - Detector, Smoke | D. Detection and Alarm - Fire Protection | Detector, Smoke |  | Detector, Smoke | Each detector | On unit | A device connected to a fire alarm system that detects visible or invisible particles of combustion. (SIG-IDS) |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 46 | Smoke Detection Sensors | 23-29 29 13 11 | Smoke Detectors
Asset | D7050.10 | Not on One-Line | D7050.10 - Detection and Alarm - Fire Protection - Emergency services notification transmission equipment | D7050.10 - Detection and Alarm - Fire Protection | Emergency services notification transmission equipment |  | D. Detection and Alarm - Fire Protection - Emergency services notification transmission equipment | D. Detection and Alarm - Fire Protection | Emergency services notification transmission equipment |  | Emergency services notification transmission equipment | Each unit | On unit | An automated function of the fire alarm panel that sends an alarm to central office location. This is typically tracked as a component, and not its own asset. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 23 | Fire Detection and Alarm Annunciation Panels and Fire Stations | 23-29 31 00 | Fire Notification Appliances
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Fire Alarm Central Station | D7050.10 - Detection and Alarm - Fire Protection | Fire Alarm Central Station |  | D. Detection and Alarm - Fire Protection - Fire Alarm Central Station | D. Detection and Alarm - Fire Protection | Fire Alarm Central Station |  | Fire Alarm Central Station | Each panel | On panel | NFPA defines this as “a system or group of systems in which the operations of circuits and devices are transmitted automatically to, recorded in, maintained by, and supervised from a listed central station that has competent and experienced servers and operators who, upon receipt of a signal, take such action as required by NFPA 72. Such service is to be controlled and operated by a person, firm, or corporation whose business is the furnishing, maintaining, or monitoring of supervised alarm systems.” |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 | Fire Detection and Alarm Interfaces | 23-29 31 23 | Fire Alarm Central Stations
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Fire Alarm Control Panel | D7050.10 - Detection and Alarm - Fire Protection | Fire Alarm Control Panel |  | D. Detection and Alarm - Fire Protection - Fire Alarm Control Panel | D. Detection and Alarm - Fire Protection | Fire Alarm Control Panel |  | Fire Alarm Control Panel | Each panel/node | On panel/node | A fire alarm control panel (FACP), fire alarm control unit (FACU), or simply fire alarm panel is the controlling component of a fire alarm system. The panel receives information from devices designed to detect and report fires, monitors their operational integrity and provides for automatic control of equipment, and transmission of information necessary to prepare the facility for fire based on a predetermined sequence. The panel may also supply electrical energy to operate any associated initiating device, notification appliance, control, transmitter, or relay. There are four basic types of panels: coded panels, conventional panels, addressable panels, and multiplex systems. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 | Fire Detection and Alarm Interfaces | 23-29 31 13 15 | Fire Alarm Audio Control Panels
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Fire Alarm Control Panel Batteries | D7050.10 - Detection and Alarm - Fire Protection | Fire Alarm Control Panel Batteries |  | D. Detection and Alarm - Fire Protection - Fire Alarm Control Panel Batteries | D. Detection and Alarm - Fire Protection | Fire Alarm Control Panel Batteries |  | Fire Alarm Control Panel Batteries | Each unit | On unit | A secondary power source of failure of the AC hardwired power. Smaller capacity units are typically mounted within the alarm panel but as capacity increases they will often have their own cabinet. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 16 | Fire Detection and Alarm Interfaces to Access Control Hardware | 23-29 31 13 13 | Secondary Fire Alarm Control Panels
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Fire Alarm Panel - Booster Power Supply | D7050.10 - Detection and Alarm - Fire Protection | Fire Alarm Panel - Booster Power Supply |  | D. Detection and Alarm - Fire Protection - Fire Alarm Panel - Booster Power Supply | D. Detection and Alarm - Fire Protection | Fire Alarm Panel - Booster Power Supply |  | Fire Alarm Panel - Booster Power Supply | Each panel/node | On panel/node | Extends the power capabilities of existing notification appliance circuits as well as provides power for other ancillary devices. This is typically tracked as a component of the panel, and not as its own asset. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 16 | Fire Detection and Alarm Interfaces to Access Control Hardware | 23-29 31 13 13 | Secondary Fire Alarm Control Panels
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Fire Alarm Panel - Data Gathering Panel (DGP) | D7050.10 - Detection and Alarm - Fire Protection | Fire Alarm Panel - Data Gathering Panel (DGP) |  | D. Detection and Alarm - Fire Protection - Fire Alarm Panel - Data Gathering Panel (DGP) | D. Detection and Alarm - Fire Protection | Fire Alarm Panel - Data Gathering Panel (DGP) |  | Fire Alarm Panel - Data Gathering Panel (DGP) | Each panel/node | On panel/node | A data gathering panel (DGP) allows inputs and relays to be connected at a location remote from the challenger panel. Data gathering panels are used to expand the number of inputs and outputs in a system and to send data to the challenger panel for processing. Standard with a data gathering panel is 8 inputs, 8 open collectors and a siren driver, however this is expandable to a total of 32 inputs and 16 relays/outputs. Should a failure in communications occur, the data gathering panel remembers the last alarm in a system, helping to identify possible reasons for faults. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 16 | Fire Detection and Alarm Interfaces to Access Control Hardware | 23-29 31 25 | Fire Alarm Event Recorders
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Fire Fighter Phone | D7050.10 - Detection and Alarm - Fire Protection | Fire Fighter Phone |  | D. Detection and Alarm - Fire Protection - Fire Fighter Phone | D. Detection and Alarm - Fire Protection | Fire Fighter Phone |  | Fire Fighter Phone | Each unit | On unit | A dedicated communication network connecting various points in a building with a central point such as the fire wardens station. May have wired handsets or jacks for phone sets carried by the firefighter. This is typically tracked as a component of the station, and not its own asset. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-27 32 26 | Ring-Down Emergency Telephones | 23-29 31 21 | Fire Alarm Communicators
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Fire Fighter Smoke Control Panel | D7050.10 - Detection and Alarm - Fire Protection | Fire Fighter Smoke Control Panel |  | D. Detection and Alarm - Fire Protection - Fire Fighter Smoke Control Panel | D. Detection and Alarm - Fire Protection | Fire Fighter Smoke Control Panel |  | Fire Fighter Smoke Control Panel | Each panel | On panel | A panel that provides the firefighter with monitoring and control of the building's smoke control system. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 23 | Fire Detection and Alarm Interfaces to Access Control System | 23-29 31 13 17 | Fire Alarm Smoke Control Panels
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Horn Audible Device | D7050.10 - Detection and Alarm - Fire Protection | Horn Audible Device |  | D. Detection and Alarm - Fire Protection - Horn Audible Device | D. Detection and Alarm - Fire Protection | Horn Audible Device |  | Horn Audible Device | Each unit | On unit | A fire alarm notification appliance is an active fire protection component of a fire alarm system. A horn audible device uses audible stimuli to alert the occupants of a fire or other emergency condition requiring action. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 63 13 | Fire Alarm Horns and Strobes | 23-29 31 15 13 | Audible Fire Notification Devices Horn
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Horn/Strobe Combo | D7050.10 - Detection and Alarm - Fire Protection | Horn/Strobe Combo |  | D. Detection and Alarm - Fire Protection - Horn/Strobe Combo | D. Detection and Alarm - Fire Protection | Horn/Strobe Combo |  | Horn/Strobe Combo | Each unit | On unit | A fire alarm notification appliance is an active fire protection component of a fire alarm system. A horn/strobe appliance uses audible, visible stimuli to alert the occupants of a fire or other emergency condition requiring action. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 63 13 | Fire Alarm Horns and Strobes | 23-29 31 19 | Combination Audible and Visible Fire Notification Devices
Asset | D7050.10 | D40-1 | D7050.10 - Detection and Alarm - Fire Protection - Low Air Pressure Switch | D7050.10 - Detection and Alarm - Fire Protection | Low Air Pressure Switch |  | D. Detection and Alarm - Fire Protection - Low Air Pressure Switch | D. Detection and Alarm - Fire Protection | Low Air Pressure Switch |  | Low Air Pressure Switch | Each unit | On unit | These switches watch for a loss of air in a dry-pipe system. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 33 16 | Fire Detection and Alarm Interfaces to Access Control Hardware | 23-29 29 15 | Fire Switches
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Pull Station | D7050.10 - Detection and Alarm - Fire Protection | Pull Station |  | D. Detection and Alarm - Fire Protection - Pull Station | D. Detection and Alarm - Fire Protection | Pull Station |  | Pull Station | Each unit | On unit | A button, lever, or other device in a building used to set off the fire alarm when manually pulled, or pushed. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 53 13 | Fire Alarm Pull Stations | 23-29 29 11 | Fire Alarm Pull Stations
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Speaker Audible Device | D7050.10 - Detection and Alarm - Fire Protection | Speaker Audible Device |  | D. Detection and Alarm - Fire Protection - Speaker Audible Device | D. Detection and Alarm - Fire Protection | Speaker Audible Device |  | Speaker Audible Device | Each unit | On unit | This is a notification appliance which the NFPA defines as “a fire alarm system component such as a bell, horn, speaker, light, or text display that provides audible, tactile, or visible outputs, or any combination thereof.” |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 53 23 | Fire Alarm Level Detectors Switches | 23-29 31 15 | Audible Fire Notification Devices
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Strobe Light | D7050.10 - Detection and Alarm - Fire Protection | Strobe Light |  | D. Detection and Alarm - Fire Protection - Strobe Light | D. Detection and Alarm - Fire Protection | Strobe Light |  | Strobe Light | Each unit | On unit | A fire alarm notification appliance that uses a pulsing light to alert occupants that the fire alarm system has detected a problem. These devices are meant to help alert hearing impaired individuals in the event of a fire. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 63 13 | Fire Alarm Horns and Strobes | 23-29 31 17 | Visible Fire Notification Devices
Asset | D7050.10 | D70-1 | D7050.10 - Detection and Alarm - Fire Protection - Tamper Switch | D7050.10 - Detection and Alarm - Fire Protection | Tamper Switch |  | D. Detection and Alarm - Fire Protection - Tamper Switch | D. Detection and Alarm - Fire Protection | Tamper Switch |  | Tamper Switch | Each unit | On unit | A sensor on a manual cutoff valve in a fire sprinkler system that provides a supervisory alarm signal to the fire alarm system if the valve is tampered with. |  | 21-04 70 50 10 | Fire Detection and Alarm | 22-28 31 53 33 | Fire Alarm Flow Switches | 23-29 29 15 15 | Fire Tamper Switches
Supplemental Elements | D7050.10.99 | n/a | D7050.10 - Detection and Alarm - Fire Protection - [Supplemental Elements] Fire Alarm | D7050.10 - Detection and Alarm - Fire Protection | [Supplemental Elements] Fire Alarm |  | D. Detection and Alarm - Fire Protection - [Supplemental Elements] Fire Alarm | D. Detection and Alarm - Fire Protection | [Supplemental Elements] Fire Alarm |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D7050.20 |  | D7050.20 - Detection and Alarm - Radiation | D7050.20 - Detection and Alarm - Radiation |  |  | D. Detection and Alarm - Radiation | D. Detection and Alarm - Radiation | [5 empty] | General Category |  | 21-04 70 50 20 | Radiation Detection and Alarm | 22-28 32 00 | Radiation Detection and Alarm | 23-25 63 13 35 | Radiation Detection Or Monitoring Products
Asset | D7050.20 | Not on One-Line | D7050.20 - Detection and Alarm - Radiation - Radiation Detection and Protection | D7050.20 - Detection and Alarm - Radiation | Radiation Detection and Protection |  | D. Detection and Alarm - Radiation - Radiation Detection and Protection | D. Detection and Alarm - Radiation | Radiation Detection and Protection |  | Radiation Detection and Protection | Each detector | Track by system | This is a system normally set up at a garbage discharge point of a hospital to catch waste that may be contaminated by radioactive material. The system gives off an audio/visual alarm when radiation is detected. |  | 21-04 70 50 20 | Radiation Detection and Alarm | 22-28 32 33 | Radiation Detection Sensors | 23-25 63 13 35 15 | Radiation Detectors
Grouping | D7050.40 |  | D7050.20 - Detection and Alarm - Fuel-Oil | D7050.20 - Detection and Alarm - Fuel-Oil |  |  | D. Detection and Alarm - Fuel-Oil | D. Detection and Alarm - Fuel-Oil | [5 empty] | General Category |  | 21-04 70 50 20 | Radiation Detection and Alarm | 22-28 32 00 | Radiation Detection and Alarm | 23-25 63 13 35 | Radiation Detection Or Monitoring Products
Asset | D7050.40 | G30-1 | D7050.20 - Detection and Alarm - Fuel-Oil - Detection & Alarm Package | D7050.20 - Detection and Alarm - Fuel-Oil | Detection & Alarm Package |  | D. Detection and Alarm - Fuel-Oil - Detection & Alarm Package | D. Detection and Alarm - Fuel-Oil | Detection & Alarm Package |  | Fuel-Oil Detection and Alarm | Each Unit | Track by system | This is a detection and monitoring system that senses through several possible technologies the presence or suspected presence of oil outside the tank. |  | 21-04 70 50 20 | Radiation Detection and Alarm | 22-28 32 33 | Radiation Detection Sensors | 23-25 63 13 35 15 | Radiation Detectors
Grouping | D7050.50 |  | D7050.50 - Detection and Alarm - Refrigeration | D7050.50 - Detection and Alarm - Refrigeration |  |  | D. Detection and Alarm - Refrigeration | D. Detection and Alarm - Refrigeration | [5 empty] | General Category |  | 21-04 70 50 50 | Refrigeration Detection and Alarm | 22-28 35 00 | Refrigerant Detection and Alarm | 23-33 51 11 | Refrigerant Monitors
Asset | D7050.50 | Not on One-Line | D7050.50 - Detection and Alarm - Refrigeration - Detector, Refrigerant Leak | D7050.50 - Detection and Alarm - Refrigeration | Detector, Refrigerant Leak |  | D. Detection and Alarm - Refrigeration - Detector, Refrigerant Leak | D. Detection and Alarm - Refrigeration | Detector, Refrigerant Leak |  | Refrigerant Leak Detector | Each detection system | Track by system | Refrigerant monitors detecting levels as low as 1 ppm can detect refrigerant leaks early in machinery rooms, from display cases on the store floor and in storage areas, helping to protect produce and deliver efficient refrigeration. |  | 21-04 70 50 50 | Refrigeration Detection and Alarm | 22-28 35 33 | Refrigerant Detection Sensors | 23-33 51 11 | Refrigerant Monitors
Asset | D7050.50 | Not on One-Line | D7050.50 - Detection and Alarm - Refrigeration - Refrigerator Temperature Alarm | D7050.50 - Detection and Alarm - Refrigeration | Refrigerator Temperature Alarm |  | D. Detection and Alarm - Refrigeration - Refrigerator Temperature Alarm | D. Detection and Alarm - Refrigeration | Refrigerator Temperature Alarm |  | Refrigerator Temperature Alarm | Each alarm unit | Track by system | A temperature sensor with alarm indication used typically on lab refrigerators and freezers. Often connected to a building automation system. |  | 21-04 70 50 50 | Refrigeration Detection and Alarm | 22-28 35 33 | Refrigerant Detection Sensors | 23-27 11 11 23 | Temperature Sensors
Grouping | D7050.60 |  | D7050.60 - Detection and Alarm - Water | D7050.60 - Detection and Alarm - Water |  |  | D. Detection and Alarm - Water | D. Detection and Alarm - Water | [5 empty] | General Category |  | 21-04 70 50 60 | Water Intrusion Detection and Alarm | 22-28 36 00 | Water Detection and Alarm
Asset | D7050.60 | Not on One-Line | D7050.60 - Detection and Alarm - Water - Water Sensor | D7050.60 - Detection and Alarm - Water | Water Sensor |  | D. Detection and Alarm - Water - Water Sensor | D. Detection and Alarm - Water | Water Sensor |  | Water Sensor | Per system | Track by system | Water intrusion alarms (where existing, most likely localized). |  | 21-04 70 50 60 | Water Intrusion Detection and Alarm | 22-28 36 33 | Water Detection Sensors | 23-29 39 15 13 13 | Water Leak Detection
Grouping | D7050.70 |  | D7050.70 - Detection and Alarm - Medical Gas | D7050.70 - Detection and Alarm - Medical Gas |  |  | D. Detection and Alarm - Medical Gas | D. Detection and Alarm - Medical Gas | [5 empty] | General Category |  | 21-04 80 10 40 | Integrated Automation Control of Plumbing Systems | 22-25 54 00 |  | 23-27 11 27 11 | Gas Alarm Modules
Asset | D7050.70 | D20-6 | D7050.70 - Detection and Alarm - Medical Gas - Medical Gas Alarm Panel - Area | D7050.70 - Detection and Alarm - Medical Gas | Medical Gas Alarm Panel - Area |  | D. Detection and Alarm - Medical Gas - Medical Gas Alarm Panel - Area | D. Detection and Alarm - Medical Gas | Medical Gas Alarm Panel - Area |  | Medical Gas Alarm Panel - Area ([Area Served]) | Each panel | On panel cover | This is an alarm panel that is normally located in the nurse's station that monitors the medical gas system pressures for the area served by the nurse's station and sends out an alarm when the pressures go out of range. |  | 21-04 80 10 40 | Integrated Automation Control of Plumbing Systems | 22-25 34 00 | Integrated Automation Instrumentation and Terminal Devices for Plumbing | 23-25 33 13 | Medical Gas Alarm Modules
Asset | D7050.70 | D20-6 | D7050.70 - Detection and Alarm - Medical Gas - Medical Gas Alarm Panel - Master | D7050.70 - Detection and Alarm - Medical Gas | Medical Gas Alarm Panel - Master |  | D. Detection and Alarm - Medical Gas - Medical Gas Alarm Panel - Master | D. Detection and Alarm - Medical Gas | Medical Gas Alarm Panel - Master |  | Medical Gas Alarm Panel - Master ([Area Served]) | Each panel | On panel cover | This is an alarm panel that is normally located in the security office and boiler plant, that monitors the medical gas system pressures and sends out an alarm when the pressures go out of range. |  | 21-04 80 10 40 | Integrated Automation Control of Plumbing Systems | 22-25 34 00 | Integrated Automation Instrumentation and Terminal Devices for Plumbing | 23-25 33 13 | Medical Gas Alarm Modules
Asset | D7050.70 | Not on One-Line | D7050.70 - Detection and Alarm - Medical Gas - Oxygen Monitor | D7050.70 - Detection and Alarm - Medical Gas | Oxygen Monitor |  | D. Detection and Alarm - Medical Gas - Oxygen Monitor | D. Detection and Alarm - Medical Gas | Oxygen Monitor |  | Oxygen Monitor | Each panel | On panel cover | This is a device that monitors the oxygen levels in a room and sends out an alarm when the levels fall below a setpoint. |  | 21-04 80 10 40 | Integrated Automation Control of Plumbing Systems | 22-25 34 00 | Integrated Automation Instrumentation and Terminal Devices for Plumbing | 23-27 11 27 17 19 | Oxygen Detectors | 13-51 21 27 | MRI Scanning Room
Supplemental Elements | D7050.70.99 | n/a | D7050.70 - Detection and Alarm - Medical Gas - [Supplemental Elements] Medical Gas Alarm | D7050.70 - Detection and Alarm - Medical Gas | [Supplemental Elements] Medical Gas Alarm |  | D. Detection and Alarm - Medical Gas - [Supplemental Elements] Medical Gas Alarm | D. Detection and Alarm - Medical Gas | [Supplemental Elements] Medical Gas Alarm |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | D8010 | Not on One-Line | D8010.00 - Integrated Automation | D8010.00 - Integrated Automation |  |  | D. Integrated Automation | D. Integrated Automation | [5 empty] | General Category |  | 21-04 80 10 41 | Integrated Automation Control of Plumbing Systems | 22-25 34 01 | Integrated Automation Instrumentation and Terminal Devices for Plumbing | 23-27 11 27 17 20 | Oxygen Detectors | 13-51 21 28 | MRI Scanning Room
System | D8010 | Not on One-Line | D8010.00 - Integrated Automation - (System) Integrated Automation Facilities Controls | D8010.00 - Integrated Automation | (System) Integrated Automation Facilities Controls |  | D. Integrated Automation - (System) Integrated Automation Facilities Controls | D. Integrated Automation | (System) Integrated Automation Facilities Controls |  | SYS Integrated Automation Facilities Controls ([Area Served]) | System | Track by Location | An monitoring and control system utilized to automate operation of HVAC assets. An interface is provided to view and adjust the system. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Supplemental Elements | D8010.99 | n/a | D8010.00 - Integrated Automation - [Supplemental Elements] Integrated Automation Facilities Control | D8010.00 - Integrated Automation | [Supplemental Elements] Integrated Automation Facilities Control |  | D. Integrated Automation - [Supplemental Elements] Integrated Automation Facilities Control | D. Integrated Automation | [Supplemental Elements] Integrated Automation Facilities Control |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1010.10 |  | E1010.10 - Equipment, Vehicles | E1010.10 - Equipment, Vehicles |  |  | E. Equipment - Vehicles | E. Equipment - Vehicles | [5 empty] | General Category |  | 21-05 10 | Equipment | 22-11 10 00
System | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - (System) Vehicles | E1010.10 - Equipment, Vehicles | (System) Vehicles |  | E. Equipment - Vehicles - (System) Vehicles | E. Equipment - Vehicles | (System) Vehicles |  | SYS Vehicles Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Bus/RV | E1010.10 - Equipment, Vehicles | Bus/RV |  | E. Equipment - Vehicles - Bus/RV | E. Equipment - Vehicles | Bus/RV |  | Bus/RV | Each unit | On equipment | This is a road vehicle that is used to transport a group of people from one location to another. Vehicle can also be used as a mobile office or to provide remote medical services. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Car | E1010.10 - Equipment, Vehicles | Car |  | E. Equipment - Vehicles - Car | E. Equipment - Vehicles | Car |  | Car | Each unit | On equipment | A road vehicle, typically with four wheels, powered by an internal combustion engine or electric motors and able to carry a small number of people. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Floor Scrubber | E1010.10 - Equipment, Vehicles | Floor Scrubber |  | E. Equipment - Vehicles - Floor Scrubber | E. Equipment - Vehicles | Floor Scrubber |  | Floor Scrubber | Each unit | On equipment, visible to equipment operator | A walk behind or ridden wheeled unit that cleans floors through use of fluids, rotating brushes and vacuuming. May be electric or propane powered. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Forklift | E1010.10 - Equipment, Vehicles | Forklift |  | E. Equipment - Vehicles - Forklift | E. Equipment - Vehicles | Forklift |  | Forklift | Each unit | On equipment | A vehicle with a pronged device in front for lifting and carrying heavy loads. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Garage sweeper | E1010.10 - Equipment, Vehicles | Garage sweeper |  | E. Equipment - Vehicles - Garage sweeper | E. Equipment - Vehicles | Garage sweeper |  | Garage sweeper | Each unit | On equipment | A special purpose vehicle designed to collect debris from road surfaces when in motion and utilizes a system of rotating brushes, vacuum and storage bin. Typically a small unlicensed vehicle. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 11 26 | Vehicle-Washing Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Golf Cart | E1010.10 - Equipment, Vehicles | Golf Cart |  | E. Equipment - Vehicles - Golf Cart | E. Equipment - Vehicles | Golf Cart |  | Golf Cart | Each unit | On equipment | A small motorized (gas or electric) vehicle for golfers and their equipment. Can also be used by facilities to get around a campus environment. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Motorized Vehicles | E1010.10 - Equipment, Vehicles | Motorized Vehicles |  | E. Equipment - Vehicles - Motorized Vehicles | E. Equipment - Vehicles | Motorized Vehicles |  | Motorized Vehicles | Each Vehicle | By license plate | A road vehicle, typically with four wheels, powered by an internal combustion engine or electric motor)s_ and able to carry a small number of people. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Moveable scissor lift | E1010.10 - Equipment, Vehicles | Moveable scissor lift |  | E. Equipment - Vehicles - Moveable scissor lift | E. Equipment - Vehicles | Moveable scissor lift |  | Moveable scissor lift | Each unit | On equipment, visible to equipment operator | A mobile vertical personnel lift typically hydraulically actuated that raises a platform supported on a scissor type elevated frame. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Parking Lot Sweeper | E1010.10 - Equipment, Vehicles | Parking Lot Sweeper |  | E. Equipment - Vehicles - Parking Lot Sweeper | E. Equipment - Vehicles | Parking Lot Sweeper |  | Parking Lot Sweeper | Each unit | On equipment, visible to equipment operator | A special purpose vehicle designed to collect debris from road surfaces when in motion and utilizes a system of rotating brushes, vacuum and storage bin. May be a small unlicensed vehicle or an over the road truck. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 11 26 | Vehicle-Washing Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Payloader | E1010.10 - Equipment, Vehicles | Payloader |  | E. Equipment - Vehicles - Payloader | E. Equipment - Vehicles | Payloader |  | Payloader | Each unit | On equipment, visible to equipment operator | A large rubber tired earth mover with a single front bucket. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Scooter | E1010.10 - Equipment, Vehicles | Scooter |  | E. Equipment - Vehicles - Scooter | E. Equipment - Vehicles | Scooter |  | Scooter | Each unit | On equipment, visible to equipment operator | A small unlicensed personnel carrier for one or two people often three wheeled and electric powered. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Snow Plow | E1010.10 - Equipment, Vehicles | Snow Plow |  | E. Equipment - Vehicles - Snow Plow | E. Equipment - Vehicles | Snow Plow |  | Snow Plow | Each unit | On equipment | An accessory that is mounted on a vehicle that is used for clearing roads of snow by pushing it aside. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - SUV | E1010.10 - Equipment, Vehicles | SUV |  | E. Equipment - Vehicles - SUV | E. Equipment - Vehicles | SUV |  | SUV | Each unit | On equipment, visible to equipment operator | A sport utility vehicle. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Tow Motor | E1010.10 - Equipment, Vehicles | Tow Motor |  | E. Equipment - Vehicles - Tow Motor | E. Equipment - Vehicles | Tow Motor |  | Tow Motor | Each unit | On equipment, visible to equipment operator | Powered vehicles, tugs, industrial tractors, and forklifts that are often referred to generically at the manufacturer's brand, Tow Motors. Can be eclectic, gas or diesel powered. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Tractor | E1010.10 - Equipment, Vehicles | Tractor |  | E. Equipment - Vehicles - Tractor | E. Equipment - Vehicles | Tractor |  | Tractor | Each unit | On equipment, visible to equipment operator | A powerful motorized vehicle with large rear wheels, used for hauling equipment and trailers. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Truck | E1010.10 - Equipment, Vehicles | Truck |  | E. Equipment - Vehicles - Truck | E. Equipment - Vehicles | Truck |  | Truck | Each unit | On equipment, visible to equipment operator | A large, heavy motorized (gas or diesel) vehicle used for transporting goods and materials. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Van | E1010.10 - Equipment, Vehicles | Van |  | E. Equipment - Vehicles - Van | E. Equipment - Vehicles | Van |  | Van | Each unit | On equipment, visible to equipment operator | A licensed over the road vehicle for passenger transport of moving cargo. |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.10 | Not on One-Line | E1010.10 - Equipment, Vehicles - Vehicle Servicing Equipment | E1010.10 - Equipment, Vehicles | Vehicle Servicing Equipment |  | E. Equipment - Vehicles - Vehicle Servicing Equipment | E. Equipment - Vehicles | Vehicle Servicing Equipment |  | Vehicle Servicing Equipment | Each unit | On equipment | Any equipment utilized for maintenance of vehicles of any size including over the road cars and trucks, forklifts, tow motors etc. |  | 21-05 10 10 10 | Vehicle Servicing Equipment | 22-11 11 00 | Vehicle Service Equipment
Supplemental Elements | E1010.10.99 | n/a | E1010.10 - Equipment, Vehicles - [Supplemental Elements] Vehicles | E1010.10 - Equipment, Vehicles | [Supplemental Elements] Vehicles |  | E. Equipment - Vehicles - [Supplemental Elements] Vehicles | E. Equipment - Vehicles | [Supplemental Elements] Vehicles |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1010.30 |  | E1010.30 - Equipment, Parking Control | E1010.30 - Equipment, Parking Control |  |  | E. Equipment - Parking Control | E. Equipment - Parking Control | [5 empty] | General Category |  | 21-05 10 10 50 | Loading Dock Equipment | 22-11 13 00 | Loading Dock Equipment
Asset | E1010.30 | Not on One-Line | E1010.30 - Equipment, Parking Control - Parking Gate | E1010.30 - Equipment, Parking Control | Parking Gate |  | E. Equipment - Parking Control - Parking Gate | E. Equipment - Parking Control | Parking Gate |  | Parking Gate | Each unit | On unit | An mechanized barrier utilized to control vehicular access to parking lots and garages.
System | E1010.30 | Not on One-Line | E1010.10 - Equipment, Vehicles - (System) Parking Control | E1010.10 - Equipment, Vehicles | (System) Parking Control |  | E. Equipment - Vehicles - (System) Parking Control | E. Equipment - Vehicles | (System) Parking Control |  | SYS Parking Control Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Supplemental Elements | E1010.30.99 | n/a | E1010.30 - Equipment, Parking Control - [Supplemental Elements] Parking Control | E1010.30 - Equipment, Parking Control | [Supplemental Elements] Parking Control |  | E. Equipment - Parking Control - [Supplemental Elements] Parking Control | E. Equipment - Parking Control | [Supplemental Elements] Parking Control |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1010.50 |  | E1010.50 - Equipment, Loading Dock | E1010.50 - Equipment, Loading Dock |  |  | E. Equipment - Loading Dock | E. Equipment - Loading Dock | [5 empty] | General Category |  | 21-05 10 10 50 | Loading Dock Equipment | 22-11 13 00 | Loading Dock Equipment
System | E1010.50 | Not on One-Line | E1010.50 - Equipment, Loading Dock - (System) Loading Dock | E1010.50 - Equipment, Loading Dock | (System) Loading Dock |  | E. Equipment - Loading Dock - (System) Loading Dock | E. Equipment - Loading Dock | (System) Loading Dock |  | SYS Loading Dock Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1010.50 | Not on One-Line | E1010.50 - Equipment, Loading Dock - Loading Dock Leveler | E1010.50 - Equipment, Loading Dock | Loading Dock Leveler |  | E. Equipment - Loading Dock - Loading Dock Leveler | E. Equipment - Loading Dock | Loading Dock Leveler |  | Loading Dock Leveler | Each unit | On control panel | This is a movable portion of the loading dock that allows for different vehicle heights to be offloaded on to the dock. |  | 21-05 10 10 50 | Loading Dock Equipment | 22-11 13 19 13 | Loading Dock Levelers
Supplemental Elements | E1010.50.99 | n/a | E1010.50 - Equipment, Loading Dock - [Supplemental Elements] Loading Dock | E1010.50 - Equipment, Loading Dock | [Supplemental Elements] Loading Dock |  | E. Equipment - Loading Dock - [Supplemental Elements] Loading Dock | E. Equipment - Loading Dock | [Supplemental Elements] Loading Dock |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1030.35 |  | E1030.35 - Equipment, Laundry | E1030.35 - Equipment, Laundry |  |  | E. Equipment - Laundry | E. Equipment - Laundry | [5 empty] | General Category |  | 21-05 10 30 35 | Commercial Laundry and Dry Cleaning Equipment | 22-11 23 00 | Commercial Laundry and Dry Cleaning Equipment
System | E1030.35 | Not on One-Line | E1030.35 - Equipment, Laundry - (System) Laundry | E1030.35 - Equipment, Laundry | (System) Laundry |  | E. Equipment - Laundry - (System) Laundry | E. Equipment - Laundry | (System) Laundry |  | SYS Laundry Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1030.35 | Not on One-Line | E1030.35 - Equipment, Laundry - Laundry and Dry Cleaning Equipment | E1030.35 - Equipment, Laundry | Laundry and Dry Cleaning Equipment |  | E. Equipment - Laundry - Laundry and Dry Cleaning Equipment | E. Equipment - Laundry | Laundry and Dry Cleaning Equipment |  | Laundry and Dry Cleaning Equipment | Each unit | On equipment | Commercial Laundry and Dry Cleaning Equipment |  | 21-05 10 30 35 | Commercial Laundry and Dry Cleaning Equipment | 22-11 23 00 | Commercial Laundry and Dry Cleaning Equipment
Supplemental Elements | E1030.35.99 | n/a | E1030.35 - Equipment, Laundry - [Supplemental Elements] Laundry | E1030.35 - Equipment, Laundry | [Supplemental Elements] Laundry |  | E. Equipment - Laundry - [Supplemental Elements] Laundry | E. Equipment - Laundry | [Supplemental Elements] Laundry |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1030.40 |  | E1030.40 - Equipment, Maintenance | E1030.40 - Equipment, Maintenance |  |  | E. Equipment - Maintenance | E. Equipment - Maintenance | [5 empty] | General Category |  |  |  | 22-11 01 00 | Operation and Maintenance of Equipment
System | E1030.40 | Not on One-Line | E1030.40 - Equipment, Maintenance - (System) Maintenance | E1030.40 - Equipment, Maintenance | (System) Maintenance |  | E. Equipment - Maintenance - (System) Maintenance | E. Equipment - Maintenance | (System) Maintenance |  | SYS Maintenance Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1030.40 | Not on One-Line | E1030.40 - Equipment, Maintenance - Battery Charger | E1030.40 - Equipment, Maintenance | Battery Charger |  | E. Equipment - Maintenance - Battery Charger | E. Equipment - Maintenance | Battery Charger |  | Battery Charger | Each unit | On charger | An inverter, almost always automatic in operation for charging and maintaining a charge in batteries of various types. Generally only larger or critical units are considered assets such as used for station switchgear or central emergency lighting applications.
Asset | E1030.40 | Not on One-Line | E1030.40 - Equipment, Maintenance - Maintenance Carts | E1030.40 - Equipment, Maintenance | Maintenance Carts |  | E. Equipment - Maintenance - Maintenance Carts | E. Equipment - Maintenance | Maintenance Carts |  | Maintenance Carts | Each unit | On equipment | Generally manually rolled carts consisting of drawers and a flat work surface on top that provide parts and tool storage. They are sized to navigate through doorways and corridors. |  | 21-05 10 90 | Other Equipment | 22-11 90 00 | Other Equipment
Asset | E1030.40 | Not on One-Line | E1030.40 - Equipment, Maintenance - Maintenance Equipment | E1030.40 - Equipment, Maintenance | Maintenance Equipment |  | E. Equipment - Maintenance - Maintenance Equipment | E. Equipment - Maintenance | Maintenance Equipment |  | Maintenance Equipment | Each unit | On equipment | A group of typically power operated appliances utilized for grounds work or interior use. Typically includes mowers, leaf blowers, power washers and shop equipment. Generally, the higher cost items may be tracked as assets.
Asset | E1030.40 | Not on One-Line | E1030.40 - Equipment, Maintenance - Portable Generator | E1030.40 - Equipment, Maintenance | Portable Generator |  | E. Equipment - Maintenance - Portable Generator | E. Equipment - Maintenance | Portable Generator |  | Portable Generator | Each unit | On equipment | Portable electrical generator
Supplemental Elements | E1030.40.99 | n/a | E1030.40 - Equipment, Maintenance - [Supplemental Elements] Maintenance | E1030.40 - Equipment, Maintenance | [Supplemental Elements] Maintenance |  | E. Equipment - Maintenance - [Supplemental Elements] Maintenance | E. Equipment - Maintenance | [Supplemental Elements] Maintenance |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1030.80 |  | E1030.80 - Equipment, Foodservice | E1030.80 - Equipment, Foodservice |  |  | E. Equipment - Foodservice | E. Equipment - Foodservice | [5 empty] | General Category |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 40 00 | Foodservice Equipment
System | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - (System) Food Service | E1030.80 - Equipment, Foodservice | (System) Food Service |  | E. Equipment - Foodservice - (System) Food Service | E. Equipment - Foodservice | (System) Food Service |  | SYS Food Service Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Dishwasher | E1030.80 - Equipment, Foodservice | Dishwasher |  | E. Equipment - Foodservice - Dishwasher | E. Equipment - Foodservice | Dishwasher |  | Dishwasher | Each unit | On appliance | Dishwasher |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 40 00 | Foodservice Equipment
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Food Truck | E1030.80 - Equipment, Foodservice | Food Truck |  | E. Equipment - Foodservice - Food Truck | E. Equipment - Foodservice | Food Truck |  | Food Truck | Each unit | On equipment, visible to equipment operator | This is a vehicle that delivers food. May contain a refrigeration unit depending on the type of food that is being delivered. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 40 00 | Foodservice Equipment
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Foodservice Appliances | E1030.80 - Equipment, Foodservice | Foodservice Appliances |  | E. Equipment - Foodservice - Foodservice Appliances | E. Equipment - Foodservice | Foodservice Appliances |  | Foodservice Appliances | Each unit | On appliance | Any group of equipment used to cook heat food and may include stoves, steam kettles, grills, fryers, steam ovens etc. Energy source may be electric, gas or steam. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 44 00 | Food Cooking Equipment
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Freezer (Reach-in) | E1030.80 - Equipment, Foodservice | Freezer (Reach-in) |  | E. Equipment - Foodservice - Freezer (Reach-in) | E. Equipment - Foodservice | Freezer (Reach-in) |  | Freezer (Reach-in) | Each unit | Front of unit | Freezer (Reach-in) |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 13 | Refrigerated Food Storage Cases | 23-21 21 27 13 25 | Commercial Upright Reach In Freezers
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Freezer (Reach-in) - Breast Milk | E1030.80 - Equipment, Foodservice | Freezer (Reach-in) | Breast Milk | E. Equipment - Foodservice - Freezer (Reach-in) - Breast Milk | E. Equipment - Foodservice | Freezer (Reach-in) | Breast Milk | Freezer (Reach-in) - Breast Milk | Each unit | Front of unit | A freezer dedicated to storing breast milk only. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 13 | Refrigerated Food Storage Cases | 23-21 21 27 13 25 | Commercial Upright Reach In Freezers
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Freezer (Reach-in) - Patient Nutrition | E1030.80 - Equipment, Foodservice | Freezer (Reach-in) | Patient Nutrition | E. Equipment - Foodservice - Freezer (Reach-in) - Patient Nutrition | E. Equipment - Foodservice | Freezer (Reach-in) | Patient Nutrition | Freezer (Reach-in) - Patient Nutrition | Each unit | On appliance | A freezer dedicated to storing patient food only. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 13 | Refrigerated Food Storage Cases | 23-21 21 27 13 25 | Commercial Upright Reach In Freezers
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Freezer (Walk-in) | E1030.80 - Equipment, Foodservice | Freezer (Walk-in) |  | E. Equipment - Foodservice - Freezer (Walk-in) | E. Equipment - Foodservice | Freezer (Walk-in) |  | Freezer (Walk-in) | Each unit | On outside, next to upper door hinge | A refrigerated room or room sized box, usually found in kitchens. Consists of box, special door and refrigeration systems. This unit is a freezer. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 23 | Walk-In Coolers
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Freezer (Walk-in) - Patient Nutrition | E1030.80 - Equipment, Foodservice | Freezer (Walk-in) | Patient Nutrition | E. Equipment - Foodservice - Freezer (Walk-in) - Patient Nutrition | E. Equipment - Foodservice | Freezer (Walk-in) | Patient Nutrition | Freezer (Walk-in) - Patient Nutrition | Each unit | On outside, next to upper door hinge | A refrigerated room or room sized box, usually found in kitchens. Consists of box, special door and refrigeration systems. This unit is a freezer. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 23 | Walk-In Coolers
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Ice Machine | E1030.80 - Equipment, Foodservice | Ice Machine |  | E. Equipment - Foodservice - Ice Machine | E. Equipment - Foodservice | Ice Machine |  | Ice Machine | Each unit | On equipment | A stand-alone appliance for making ice, or an industrial machine for making ice on a large scale. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 47 00 | Ice Machines | 23-21 21 29 | Commercial Ice Machines
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Ice Machine - Bin Style | E1030.80 - Equipment, Foodservice | Ice Machine | Bin Style | E. Equipment - Foodservice - Ice Machine - Bin Style | E. Equipment - Foodservice | Ice Machine | Bin Style | Ice Machine - Bin Style | Each unit | On equipment | A stand-alone appliance for making ice, or an industrial machine for making ice on a large scale. This version is provided with a bin below the ice making component of the machine to store and retrieve the ice. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 47 00 | Ice Machines | 23-21 21 29 | Commercial Ice Machines
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Ice Machine - Dispenser | E1030.80 - Equipment, Foodservice | Ice Machine | Dispenser | E. Equipment - Foodservice - Ice Machine - Dispenser | E. Equipment - Foodservice | Ice Machine | Dispenser | Ice Machine - Dispenser | Each unit | On equipment | A stand-alone appliance for making ice, or an industrial machine for making ice on a large scale. This version is provided with a dispensing tube device to allow ice to be discarded directly into a container or cup. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 47 00 | Ice Machines | 23-21 21 29 | Commercial Ice Machines
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Refrigerator (Reach-in) | E1030.80 - Equipment, Foodservice | Refrigerator (Reach-in) |  | E. Equipment - Foodservice - Refrigerator (Reach-in) | E. Equipment - Foodservice | Refrigerator (Reach-in) |  | Refrigerator (Reach-in) | Each unit | On appliance | Refrigerator (Reach-in) |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 13 | Refrigerated Food Storage Cases | 23-21 21 27 15 23 | Commercial Upright Reach In Refrigerators
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Refrigerator (Reach-in) - Breast Milk | E1030.80 - Equipment, Foodservice | Refrigerator (Reach-in) | Breast Milk | E. Equipment - Foodservice - Refrigerator (Reach-in) - Breast Milk | E. Equipment - Foodservice | Refrigerator (Reach-in) | Breast Milk | Refrigerator (Reach-in) - Breast Milk | Each unit | Front of unit | A refrigeration unit for storing breast milk. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 13 | Refrigerated Food Storage Cases | 23-21 21 27 13 25 | Commercial Upright Reach In Freezers
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Refrigerator (Reach-in) - Patient Nutrition | E1030.80 - Equipment, Foodservice | Refrigerator (Reach-in) | Patient Nutrition | E. Equipment - Foodservice - Refrigerator (Reach-in) - Patient Nutrition | E. Equipment - Foodservice | Refrigerator (Reach-in) | Patient Nutrition | Refrigerator (Reach-in) - Patient Nutrition | Each unit | On appliance | A refrigeration unit for storing patient food only. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 13 | Refrigerated Food Storage Cases | 23-21 21 27 15 23 | Commercial Upright Reach In Refrigerators
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Refrigerator (Reach-in) - Staff Food | E1030.80 - Equipment, Foodservice | Refrigerator (Reach-in) | Staff Food | E. Equipment - Foodservice - Refrigerator (Reach-in) - Staff Food | E. Equipment - Foodservice | Refrigerator (Reach-in) | Staff Food | Refrigerator (Reach-in) - Staff Food | Each unit | On appliance | A refrigeration unit for storing staff food only. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 13 | Refrigerated Food Storage Cases | 23-21 21 27 15 23 | Commercial Upright Reach In Refrigerators
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Refrigerator (Walk-in) | E1030.80 - Equipment, Foodservice | Refrigerator (Walk-in) |  | E. Equipment - Foodservice - Refrigerator (Walk-in) | E. Equipment - Foodservice | Refrigerator (Walk-in) |  | Refrigerator (Walk-in) | Each unit | On outside, next to upper door hinge | A refrigerated room or room sized box, usually found in kitchens. Consists of box, special door, and refrigeration systems. This unit is a refrigerator. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 23 | Walk-In Coolers | 23-21 21 27 15 29 | Commercial Walk In Refrigerators
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Refrigerator (Walk-in) - Patient Nutrition | E1030.80 - Equipment, Foodservice | Refrigerator (Walk-in) | Patient Nutrition | E. Equipment - Foodservice - Refrigerator (Walk-in) - Patient Nutrition | E. Equipment - Foodservice | Refrigerator (Walk-in) | Patient Nutrition | Refrigerator (Walk-in) - Patient Nutrition | Each unit | On outside, next to upper door hinge | A refrigerated room or room sized box, usually found in kitchens. Consists of box, special door, and refrigeration systems. This unit is a refrigerator. |  | 21-05 10 30 80 | Foodservice Equipment | 22-11 41 23 | Walk-In Coolers | 23-21 21 27 15 29 | Commercial Walk In Refrigerators
Asset | E1030.80 | Not on One-Line | E1030.80 - Equipment, Foodservice - Refrigerator/Freezer Condenser | E1030.80 - Equipment, Foodservice | Refrigerator/Freezer Condenser |  | E. Equipment - Foodservice - Refrigerator/Freezer Condenser | E. Equipment - Foodservice | Refrigerator/Freezer Condenser |  | Refrigerator/Freezer Condenser | Each condenser | On Unit | This is the condenser portion of a large freezer/refrigerator which is normally installed outside the building. This condenser is sometimes treated as a separate asset, or alternatively tracked together with the large freezer/refrigerator.
Supplemental Elements | E1030.80.99 | n/a | E1030.80 - Equipment, Foodservice - [Supplemental Elements] Foodservice | E1030.80 - Equipment, Foodservice | [Supplemental Elements] Foodservice |  | E. Equipment - Foodservice - [Supplemental Elements] Foodservice | E. Equipment - Foodservice | [Supplemental Elements] Foodservice |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1040.10 |  | E1040.10 - Equipment, Lab | E1040.10 - Equipment, Lab |  |  | E. Equipment - Lab | E. Equipment - Lab | [5 empty] | General Category |  | 21-05 10 40 10 | Educational and Scientific Equipment | 22-11 53 00 | Laboratory Equipment
System | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - (System) Lab | E1040.10 - Equipment, Lab | (System) Lab |  | E. Equipment - Lab - (System) Lab | E. Equipment - Lab | (System) Lab |  | SYS Lab Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Biological Safety Cabinet | E1040.10 - Equipment, Lab | Biological Safety Cabinet |  | E. Equipment - Lab - Biological Safety Cabinet | E. Equipment - Lab | Biological Safety Cabinet |  | Biological Safety Cabinet | Each Cabinet | On Unit | A biosafety cabinet —also called a biological safety cabinet or microbiological safety cabinet—is an enclosed, ventilated laboratory workspace for safely working with materials contaminated with pathogens requiring a defined biosafety level.
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Freezer (Reach-in) - Lab | E1040.10 - Equipment, Lab | Freezer (Reach-in) - Lab |  | E. Equipment - Lab - Freezer (Reach-in) - Lab | E. Equipment - Lab | Freezer (Reach-in) - Lab |  | Freezer (Reach-in) - Lab | Each Freezer | On appliance | Commercial sized freezer unit for storing laboratory samples. Not for food storage. |  | 21-05 10 40 10 | Educational and Scientific Equipment | 22-11 53 26 | Laboratory Freezers | 23-25 65 11 19 | Biological Freezers
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Freezer (Walk-in) - Lab | E1040.10 - Equipment, Lab | Freezer (Walk-in) - Lab |  | E. Equipment - Lab - Freezer (Walk-in) - Lab | E. Equipment - Lab | Freezer (Walk-in) - Lab |  | Freezer (Walk-in) - Lab | Each Freezer | On outside, next to upper door hinge | A refrigerated room or room sized box. Consists of box, special door and refrigeration systems. This unit is a freezer and is used to store laboratory samples only. Not for food storage. |  | 21-05 10 40 10 | Educational and Scientific Equipment | 22-11 53 26 | Laboratory Freezers | 23-25 65 11 19 | Biological Freezers
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Fume Hood | E1040.10 - Equipment, Lab | Fume Hood |  | E. Equipment - Lab - Fume Hood | E. Equipment - Lab | Fume Hood |  | Fume Hood | Each hood | On upper right hand corner of hood | Typically a large piece of equipment enclosing five sides of a work area, the bottom of which is most commonly located at a standing work height. Two main types exist, ducted and recirculating (ductless). The principle is the same for both types: air is drawn in from the front (open) side of the cabinet, and either expelled outside the building or made safe through filtration and fed back into the room. This is used to: - protect the user from inhaling toxic gases (fume hoods, biosafety cabinets, glove boxes) - protect the product or experiment (biosafety cabinets, glove boxes) - protect the environment (recirculating fume hoods, certain biosafety cabinets, and any other type when fitted with appropriate filters in the exhaust airstream) |  | 21-05 10 40 10 | Educational and Scientific Equipment | 22-11 53 13 | Laboratory Fume Hoods | 23-25 69 11 15 | Laboratory Fume hoods
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Laminar Flow Hood | E1040.10 - Equipment, Lab | Laminar Flow Hood |  | E. Equipment - Lab - Laminar Flow Hood | E. Equipment - Lab | Laminar Flow Hood |  | Laminar Flow Hood | Each hood | On unit | Laminar flow hoods (a.k.a. Clean Benches) provide filtered airflow across the work area that protects the sample from airborne contamination. |  | 21-05 10 40 10 | Educational and Scientific Equipment | 22-11 53 13 | Laboratory Fume Hoods | 23-25 69 11 15 | Laboratory Fume hoods
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Refrigerator (Reach-in) - Lab | E1040.10 - Equipment, Lab | Refrigerator (Reach-in) - Lab |  | E. Equipment - Lab - Refrigerator (Reach-in) - Lab | E. Equipment - Lab | Refrigerator (Reach-in) - Lab |  | Refrigerator (Reach-in) - Lab | Each Refrigerator | On appliance | Commercial sized refrigerator unit for storing lab samples only. Not for food storage. |  | 21-05 10 40 10 | Educational and Scientific Equipment | 22-11 53 23 | Laboratory Refrigerators | 23-25 65 11 21 | Biological Refrigerators
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Refrigerator (Walk-in) - Lab | E1040.10 - Equipment, Lab | Refrigerator (Walk-in) - Lab |  | E. Equipment - Lab - Refrigerator (Walk-in) - Lab | E. Equipment - Lab | Refrigerator (Walk-in) - Lab |  | Refrigerator (Walk-in) - Lab | Each Refrigerator | On outside, next to upper door hinge | A refrigerated room or room sized box. Consists of box, special door and refrigeration systems. This unit is a refrigerator and is used to store laboratory samples only. Not for food storage. |  | 21-05 10 40 10 | Educational and Scientific Equipment | 22-11 53 23 | Laboratory Refrigerators | 23-25 65 11 21 | Biological Refrigerators
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Refrigerator/Freezer Condenser | E1040.10 - Equipment, Lab | Refrigerator/Freezer Condenser |  | E. Equipment - Lab - Refrigerator/Freezer Condenser | E. Equipment - Lab | Refrigerator/Freezer Condenser |  | Refrigerator/Freezer Condenser | Each condenser | On Unit | This is the condenser portion of a large freezer/refrigerator which is normally installed outside the building. This condenser is sometimes treated as a separate asset, or alternatively tracked together with the large freezer/refrigerator.
Asset | E1040.10 | Not on One-Line | E1040.10 - Equipment, Lab - Washer | E1040.10 - Equipment, Lab | Washer |  | E. Equipment - Lab - Washer | E. Equipment - Lab | Washer |  | Washer | Each Washer | On Unit | A unit typically used for glassware, and the like to aggressively clean. Size may range from a small hand loaded unit to ones that take rolling carts. |  | 21-05 10 40 10 | Educational and Scientific Equipment | 22-11 53 17 | Laboratory Equipment Washers
Supplemental Elements | E1040.10.99 | n/a | E1040.10 - Equipment, Lab - [Supplemental Elements] Lab | E1040.10 - Equipment, Lab | [Supplemental Elements] Lab |  | E. Equipment - Lab - [Supplemental Elements] Lab | E. Equipment - Lab | [Supplemental Elements] Lab |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1040.20 |  | E1040.20 - Equipment, Healthcare | E1040.20 - Equipment, Healthcare |  |  | E. Equipment - Healthcare | E. Equipment - Healthcare | [5 empty] | General Category |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 70 00 | Healthcare Equipment | 23-25 00 00 | Medical and Laboratory Equipment
System | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - (System) Healthcare | E1040.20 - Equipment, Healthcare | (System) Healthcare |  | E. Equipment - Healthcare - (System) Healthcare | E. Equipment - Healthcare | (System) Healthcare |  | SYS Healthcare Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Bed | E1040.20 - Equipment, Healthcare | Bed |  | E. Equipment - Healthcare - Bed | E. Equipment - Healthcare | Bed |  | Bed | Each bed | Tracked by location | A patient bed. May be manual, semi-electric or full electric. Styles may include general use, penal, psychiatric.
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Freezer (Reach-in) - Blood | E1040.20 - Equipment, Healthcare | Freezer (Reach-in) - Blood |  | E. Equipment - Healthcare - Freezer (Reach-in) - Blood | E. Equipment - Healthcare | Freezer (Reach-in) - Blood |  | Freezer (Reach-in) - Blood | Each Freezer | On appliance | Commercial sized freezer unit for storing blood. Not for food storage or any other use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-25 31 11 11 | Blood Refrigerators and Freezers
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Freezer (Reach-in) - Medication/Pharmacy | E1040.20 - Equipment, Healthcare | Freezer (Reach-in) - Medication/Pharmacy |  | E. Equipment - Healthcare - Freezer (Reach-in) - Medication/Pharmacy | E. Equipment - Healthcare | Freezer (Reach-in) - Medication/Pharmacy |  | Freezer (Reach-in) - Medication/Pharmacy | Each Freezer | On appliance | Commercial sized freezer unit for storing medications. Not for food storage or any other use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-21 21 27 13 25 | Commercial Upright Reach In Freezers
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Freezer (Walk-in) - Blood | E1040.20 - Equipment, Healthcare | Freezer (Walk-in) - Blood |  | E. Equipment - Healthcare - Freezer (Walk-in) - Blood | E. Equipment - Healthcare | Freezer (Walk-in) - Blood |  | Freezer (Walk-in) - Blood | Each Freezer | On outside, next to upper door hinge | A refrigerated room or room sized box. Consists of box, special door and refrigeration systems. This unit is a freezer and is used to store blood only. Not for food storage or any other use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-25 31 11 11 13 | Blood Freezers
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Freezer (Walk-in) - Medication/Pharmacy | E1040.20 - Equipment, Healthcare | Freezer (Walk-in) - Medication/Pharmacy |  | E. Equipment - Healthcare - Freezer (Walk-in) - Medication/Pharmacy | E. Equipment - Healthcare | Freezer (Walk-in) - Medication/Pharmacy |  | Freezer (Walk-in) - Medication/Pharmacy | Each Freezer | On upper door frame, above hinge | A refrigerated room or room sized box. Consists of box, special door and refrigeration systems. This unit is a freezer and is used to store medications only. Not for food storage or any other use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-21 21 27 13 31 | Commercial Walk In Freezers
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Operating Table | E1040.20 - Equipment, Healthcare | Operating Table |  | E. Equipment - Healthcare - Operating Table | E. Equipment - Healthcare | Operating Table |  | Operating Table | Each operating table | Tracked by location | Table on which the patient lies during a surgical procedure. Typically maintained by Clinical Engineering. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 76 00 | Operating Room Equipment | 23-25 59 11 15 | Surgical Tables
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Patient Lift | E1040.20 - Equipment, Healthcare | Patient Lift |  | E. Equipment - Healthcare - Patient Lift | E. Equipment - Healthcare | Patient Lift |  | Patient Lift | Each lift | On lift | Any specifically designed device fixed or mobile that will move a patient a short distance, such as into a hydrotherapy tank. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-23 13 11 17 | Patient Lifts
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Refrigerator - Morgue | E1040.20 - Equipment, Healthcare | Refrigerator - Morgue |  | E. Equipment - Healthcare - Refrigerator - Morgue | E. Equipment - Healthcare | Refrigerator - Morgue |  | Refrigerator - Morgue | Each fridge system | Conspicuously placed on Unit | Similar to a walk in box, a morgue refrigerator is used in a hospital (or elsewhere) for the storage of human corpses awaiting identification or removal for autopsy or respectful burial, cremation or other method. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 78 13 | Mortuary Refrigerators | 23-25 15 11 11 | Postmortem Refrigerators and Freezers
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Refrigerator (Reach-in) - Blood | E1040.20 - Equipment, Healthcare | Refrigerator (Reach-in) - Blood |  | E. Equipment - Healthcare - Refrigerator (Reach-in) - Blood | E. Equipment - Healthcare | Refrigerator (Reach-in) - Blood |  | Refrigerator (Reach-in) - Blood | Each Refrigerator | On appliance | Commercial sized refrigerator unit for storing blood. Not for food storage or any other use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-25 31 11 11 | Blood Refrigerators and Freezers
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Refrigerator (Reach-in) - Medication/Pharmacy | E1040.20 - Equipment, Healthcare | Refrigerator (Reach-in) - Medication/Pharmacy |  | E. Equipment - Healthcare - Refrigerator (Reach-in) - Medication/Pharmacy | E. Equipment - Healthcare | Refrigerator (Reach-in) - Medication/Pharmacy |  | Refrigerator (Reach-in) - Medication/Pharmacy | Each Refrigerator | On appliance | Commercial sized refrigerator unit for storing medications. Not for food storage or any other use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-21 21 27 15 23 | Commercial Upright Reach In Refrigerators
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Refrigerator (Walk-in) - Blood | E1040.20 - Equipment, Healthcare | Refrigerator (Walk-in) - Blood |  | E. Equipment - Healthcare - Refrigerator (Walk-in) - Blood | E. Equipment - Healthcare | Refrigerator (Walk-in) - Blood |  | Refrigerator (Walk-in) - Blood | Each Refrigerator | On outside, next to upper door hinge | A refrigerated room or room sized box. Consists of box, special door and refrigeration systems. This unit is a refrigerator and is used to store blood only. Not for food storage or any other use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-25 31 11 11 11 | Blood Bank Refrigerators
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Refrigerator (Walk-in) - Medication/Pharmacy | E1040.20 - Equipment, Healthcare | Refrigerator (Walk-in) - Medication/Pharmacy |  | E. Equipment - Healthcare - Refrigerator (Walk-in) - Medication/Pharmacy | E. Equipment - Healthcare | Refrigerator (Walk-in) - Medication/Pharmacy |  | Refrigerator (Walk-in) - Medication/Pharmacy | Each Refrigerator | On upper door frame, above hinge | A refrigerated room or room sized box. Consists of box, special door and refrigeration systems. This unit is a refrigerator and is used to store medications only. Not for food storage or any other use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-21 21 27 15 29 | Commercial Walk In Refrigerators
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Refrigerator/Freezer Condenser | E1040.20 - Equipment, Healthcare | Refrigerator/Freezer Condenser |  | E. Equipment - Healthcare - Refrigerator/Freezer Condenser | E. Equipment - Healthcare | Refrigerator/Freezer Condenser |  | Refrigerator/Freezer Condenser | Each condenser | On Unit | This is the condenser portion of a large freezer/refrigerator which is normally installed outside the building. This condenser is sometimes treated as a separate asset, or alternatively tracked together with the large freezer/refrigerator.
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Slush Machine | E1040.20 - Equipment, Healthcare | Slush Machine |  | E. Equipment - Healthcare - Slush Machine | E. Equipment - Healthcare | Slush Machine |  | Slush Machine | Each unit | On equipment, visible to equipment operator | This device is used in an operating room to provide fine soft crushed ice that is used in various procedures. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-21 21 25 55 | Commercial Slush Dispensers
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Surgical Boom | E1040.20 - Equipment, Healthcare | Surgical Boom |  | E. Equipment - Healthcare - Surgical Boom | E. Equipment - Healthcare | Surgical Boom |  | Surgical Boom | Each boom | On boom | Surgical Boom |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 76 00
Asset | E1040.20 | Not on One-Line | E1040.20 - Equipment, Healthcare - Warming Cabinet | E1040.20 - Equipment, Healthcare | Warming Cabinet |  | E. Equipment - Healthcare - Warming Cabinet | E. Equipment - Healthcare | Warming Cabinet |  | Warming Cabinet | Each unit | On unit | This is an appliance that is used to warm blankets for patient use. |  | 21-05 10 40 20 | Healthcare Equipment | 22-11 73 00 | Patient Care Equipment | 23-21 21 11 19 | Commercial Warming Cabinets
Supplemental Elements | E1040.20.99 | n/a | E1040.20 - Equipment, Healthcare - [Supplemental Elements] Healthcare | E1040.20 - Equipment, Healthcare | [Supplemental Elements] Healthcare |  | E. Equipment - Healthcare - [Supplemental Elements] Healthcare | E. Equipment - Healthcare | [Supplemental Elements] Healthcare |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1090.10 |  | E1090.10 - Equipment, Environmental Services | E1090.10 - Equipment, Environmental Services |  |  | E. Equipment - Environmental Services | E. Equipment - Environmental Services | [5 empty] | General Category |  | 21-05 10 30 35 | Commercial Laundry and Dry Cleaning Equipment | 22-11 23 00 | Commercial Laundry and Dry Cleaning Equipment
System | E1090.10 | Not on One-Line | E1090.10 - Equipment, Environmental Services - (System) Environmental Services | E1090.10 - Equipment, Environmental Services | (System) Environmental Services |  | E. Equipment - Environmental Services - (System) Environmental Services | E. Equipment - Environmental Services | (System) Environmental Services |  | SYS Environmental Services Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1090.10 | Not on One-Line | E1090.10 - Equipment, Environmental Services - Compactor | E1090.10 - Equipment, Environmental Services | Compactor |  | E. Equipment - Environmental Services - Compactor | E. Equipment - Environmental Services | Compactor |  | Compactor | Each unit | On unit | Any type of device designed to reduce volume of materials (trash or recycling) for efficient transport off site. Units Owned such as a cardboard compactor would receive an asset designation. For tracking vendor equipment, an asset number could be applied if facility policy allows or consider charging inspection/checks against the location.
Asset | E1090.10 | Not on One-Line | E1090.10 - Equipment, Environmental Services - Environmental Containment Unit | E1090.10 - Equipment, Environmental Services | Environmental Containment Unit |  | E. Equipment - Environmental Services - Environmental Containment Unit | E. Equipment - Environmental Services | Environmental Containment Unit |  | Environmental Containment Unit | Each unit | On equipment | Commercial Laundry and Dry Cleaning Equipment |  | 21-05 10 30 35 | Commercial Laundry and Dry Cleaning Equipment | 22-11 23 00 | Commercial Laundry and Dry Cleaning Equipment
Supplemental Elements | E1090.10.99 | n/a | E1090.10 - Equipment, Environmental Services - [Supplemental Elements] Environmental Services | E1090.10 - Equipment, Environmental Services | [Supplemental Elements] Environmental Services |  | E. Equipment - Environmental Services - [Supplemental Elements] Environmental Services | E. Equipment - Environmental Services | [Supplemental Elements] Environmental Services |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | E1090.60 |  | E1090.60 - Equipment, Decontamination/Sterilization | E1090.60 - Equipment, Decontamination/Sterilization |  |  | E. Equipment - Decon./Sterilization | E. Equipment - Decon./Sterilization | [5 empty] | General Category |  | 21-05 10 90 60 | Decontamination Equipment | 22-11 71 00 | Medical Sterilizing Equipment | 23-25 57 11 | Sterilizer Equipment
System | E1090.60 | Not on One-Line | E1090.60 - Equipment, Decontamination/Sterilization - (System) Decontamination / Sterilization | E1090.60 - Equipment, Decontamination/Sterilization | (System) Decontamination / Sterilization |  | E. Equipment - Decon./Sterilization - (System) Decontamination / Sterilization | E. Equipment - Decon./Sterilization | (System) Decontamination / Sterilization |  | SYS Decontamination / Sterilization Equipment | System | n/a | Generic representation of equipment |  | 21-05 10 10 | Vehicle and Pedestrian Equipment | 22-11 10 00 | Vehicle and Pedestrian Equipment
Asset | E1090.60 | Not on One-Line | E1090.60 - Equipment, Decontamination/Sterilization - Decontamination Tank | E1090.60 - Equipment, Decontamination/Sterilization | Decontamination Tank |  | E. Equipment - Decon./Sterilization - Decontamination Tank | E. Equipment - Decon./Sterilization | Decontamination Tank |  | Decontamination Tank | Each tank | On control panel/tank | A tank connected to a decontamination shower to collect and store the waste water so that it can be safely disposed of. Usually found in hospital emergency rooms. |  | 21-05 10 90 60 | Decontamination Equipment | 22-11 71 00 | Medical Sterilizing Equipment
Asset | E1090.60 | Not on One-Line | E1090.60 - Equipment, Decontamination/Sterilization - Drying Cabinet | E1090.60 - Equipment, Decontamination/Sterilization | Drying Cabinet |  | E. Equipment - Decon./Sterilization - Drying Cabinet | E. Equipment - Decon./Sterilization | Drying Cabinet |  | Drying Cabinet | Each unit | On unit | This device is used to dry instruments and medical devices prior to being used in various procedures. |  | 21-05 10 90 60 | Decontamination Equipment | 22-11 71 00 | Medical Sterilizing Equipment | 23-25 69 13 27 15 | Laboratory Drying Cabinets
Asset | E1090.60 | Not on One-Line | E1090.60 - Equipment, Decontamination/Sterilization - Sonic Washer | E1090.60 - Equipment, Decontamination/Sterilization | Sonic Washer |  | E. Equipment - Decon./Sterilization - Sonic Washer | E. Equipment - Decon./Sterilization | Sonic Washer |  | Sonic Washer | Each unit | On unit | A device that cleans using ultrasound (usually from 20–40 kHz) to agitate a fluid. The ultrasound can be used with just water, but use of a solvent appropriate for the item to be cleaned and the type of soiling present enhances the effect. |  | 21-05 10 90 60 | Decontamination Equipment | 22-11 71 00 | Medical Sterilizing Equipment | 23-25 57 11 25 | Powered Instrument Cleaning Devices
Asset | E1090.60 | Not on One-Line | E1090.60 - Equipment, Decontamination/Sterilization - Steam Sterilizer | E1090.60 - Equipment, Decontamination/Sterilization | Steam Sterilizer |  | E. Equipment - Decon./Sterilization - Steam Sterilizer | E. Equipment - Decon./Sterilization | Steam Sterilizer |  | Steam Sterilizer | Each unit | On unit | A device that is used to destroy microorganisms on an object by bringing it to a high temperature with steam to destroy the bacteria or other organisms. |  | 21-05 10 90 60 | Decontamination Equipment | 22-11 71 00 | Medical Sterilizing Equipment | 23-25 57 11 33 | Steam Sterilizers
Asset | E1090.60 | Not on One-Line | E1090.60 - Equipment, Decontamination/Sterilization - Tabletop Sterilizer | E1090.60 - Equipment, Decontamination/Sterilization | Tabletop Sterilizer |  | E. Equipment - Decon./Sterilization - Tabletop Sterilizer | E. Equipment - Decon./Sterilization | Tabletop Sterilizer |  | Tabletop Sterilizer | Each unit | On unit | A small sterilization unit, often electrically heated for handling small trays of instruments or lab items. |  | 21-05 10 90 60 | Decontamination Equipment | 22-11 71 00 | Medical Sterilizing Equipment | 23-25 57 11 35 | Sterilization Cabinets
Supplemental Elements | E1090.60.99 | n/a | E1090.60 - Equipment, Decontamination/Sterilization - [Supplemental Elements] Decontamination | E1090.60 - Equipment, Decontamination/Sterilization | [Supplemental Elements] Decontamination |  | E. Equipment - Decon./Sterilization - [Supplemental Elements] Decontamination | E. Equipment - Decon./Sterilization | [Supplemental Elements] Decontamination |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | F1050 |  | F1050 - Special Facility Components | F1050 - Special Facility Components |  |  | F. Special Facility Components | F. Special Facility Components | [5 empty] | General Category |  | 21-06 10 50 | Special Facility Components | 22-13 12 00 | Fountains
System | F1050 | Not on One-Line | F1050 - Special Facility Components - (System) Special Facility Component | F1050 - Special Facility Components | (System) Special Facility Component |  | F. Special Facility Components - (System) Special Facility Component | F. Special Facility Components | (System) Special Facility Component |  | SYS Special Facility Component | As needed | Tracked by location | This refers to the area around the building assets and consists primarily of roads, sidewalks, and vegetation, including lawns. |  | 21-07 20 80 | Landscaping | 22-32 01 00 | Operation and Maintenance of Exterior Improvements | 23-11 27 00 | Landscaping
System | F1050.10 | Not on One-Line | F1050 - Special Facility Components - (System) Pool | F1050 - Special Facility Components | (System) Pool |  | F. Special Facility Components - (System) Pool | F. Special Facility Components | (System) Pool |  | SYS Pool | Each pool system | Tracked by location | An artificial body of water used for recreational or therapeutic purposes. |  | 21-06 10 50 10 | Pools | 22-13 11 00 | Swimming Pools
Supplemental Elements | F1050.10.99 | n/a | F1050 - Special Facility Components - [Supplemental Elements] Pool | F1050 - Special Facility Components | [Supplemental Elements] Pool |  | F. Special Facility Components - [Supplemental Elements] Pool | F. Special Facility Components | [Supplemental Elements] Pool |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Asset | F1050.30 | Not on One-Line | F1050 - Special Facility Components - Water Feature | F1050 - Special Facility Components | Water Feature |  | F. Special Facility Components - Water Feature | F. Special Facility Components | Water Feature |  | Water Feature | Each water feature | Tracked by location | A decorative display utilizing fountains of cascading water located either inside or outside. Water is recycled. |  | 21-06 10 50 30 | Interior Water Features | 22-13 12 00 | Fountains | 23-21 37 13 17 | Interior Ornamental Fountains
Asset | F1050.40 | Not on One-Line | F1050 - Special Facility Components - Aquarium | F1050 - Special Facility Components | Aquarium |  | F. Special Facility Components - Aquarium | F. Special Facility Components | Aquarium |  | Aquarium | Each aquarium | Tracked by location | A transparent tank of water in which fish and other water creatures and plants are kept. Normally provided with a filtration system and heaters. |  | 21-06 10 50 40 | Aquariums | 22-13 13 00 | Aquariums
Supplemental Elements | F1050.40.99 | n/a | F1050 - Special Facility Components - [Supplemental Elements] Special Facility Component | F1050 - Special Facility Components | [Supplemental Elements] Special Facility Component |  | F. Special Facility Components - [Supplemental Elements] Special Facility Component | F. Special Facility Components | [Supplemental Elements] Special Facility Component |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | G2080 |  | G2010 - Site Improvements | G2010 - Site Improvements |  |  | G. Site - Improvements | G. Site - Improvements | [5 empty] | General Category |  | 21-07 00 00 | Sitework | 22-32 01 30 | Operation and Maintenance of Site Improvements
System | G2080 | Not on One-Line | G2010 - Site Improvements - (System) Grounds | G2010 - Site Improvements | (System) Grounds |  | G. Site - Improvements - (System) Grounds | G. Site - Improvements | (System) Grounds |  | SYS Grounds ([Area]) | As needed | Tracked by location | This refers to the area around the building assets and consists primarily of roads, sidewalks, and vegetation, including lawns. |  | 21-07 20 80 | Landscaping | 22-32 01 00 | Operation and Maintenance of Exterior Improvements | 23-11 27 00 | Landscaping
System | G2080.10 | Not on One-Line | G2010.10 - Site Improvements - (System) Landscape Irrigation | G2010.10 - Site Improvements | (System) Landscape Irrigation |  | G. Site - Improvements - (System) Landscape Irrigation | G. Site - Improvements | (System) Landscape Irrigation |  | SYS Landscape Irrigation ([Area Served]) | As needed | Tracked by location | This is the system that is used to water the plants and lawns for a facility. Normally consists of underground piping, sprinkler heads, controllers as well as a backflow preventer. |  | 21-07 20 80 | Landscaping | 22-32 01 80 | Operation and Maintenance of Irrigation | 23-11 27 15 11 | Irrigation Sprinklers
Supplemental Elements | G2080.10.99 | n/a | G2010.10 - Site Improvements - [Supplemental Elements] Landscape Irrigation | G2010.10 - Site Improvements | [Supplemental Elements] Landscape Irrigation |  | G. Site - Improvements - [Supplemental Elements] Landscape Irrigation | G. Site - Improvements | [Supplemental Elements] Landscape Irrigation |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Supplemental Elements | G2080.99 | n/a | G2010 - Site Improvements - [Supplemental Elements] Grounds | G2010 - Site Improvements | [Supplemental Elements] Grounds |  | G. Site - Improvements - [Supplemental Elements] Grounds | G. Site - Improvements | [Supplemental Elements] Grounds |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | G3030 |  | G3030 - Site Utilities - Storm Drainage | G3030 - Site Utilities - Storm Drainage |  |  | G. Site - Storm Drainage | G. Site - Storm Drainage | [5 empty] | General Category |  |  |  | 22-33 49 00 | Storm Drainage Structures
System | G3030 | Not on One-Line | G3030 - Site Utilities - Storm Drainage - (System) Site Storm Drain | G3030 - Site Utilities - Storm Drainage | (System) Site Storm Drain |  | G. Site - Storm Drainage - (System) Site Storm Drain | G. Site - Storm Drainage | (System) Site Storm Drain |  | SYS Site Storm Drain ([Area Served]) | As needed | Tracked by location | This is an underground system that is used to direct storm water away from people and assets. |  | 21-07 30 30 | Storm Drainage Utilities | 22-22 14 00 | Facility Storm Drainage
Supplemental Elements | G3030.99 | n/a | G3030 - Site Utilities - Storm Drainage - [Supplemental Elements] Site Storm Drainage | G3030 - Site Utilities - Storm Drainage | [Supplemental Elements] Site Storm Drainage |  | G. Site - Storm Drainage - [Supplemental Elements] Site Storm Drainage | G. Site - Storm Drainage | [Supplemental Elements] Site Storm Drainage |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | G3060 |  | G3060 - Fuel Distribution | G3060 - Fuel Distribution |  |  | G. Fuel Distribution | G. Fuel Distribution | [5 empty] | General Category |  |  |  | 22-33 50 00 | Fuel Distribution Utilities
System | G3060 | Not on One-Line | G3060 - Fuel Distribution - (System) Fuel Polishing System | G3060 - Fuel Distribution | (System) Fuel Polishing System |  | G. Fuel Distribution - (System) Fuel Polishing System | G. Fuel Distribution | (System) Fuel Polishing System |  | SYS Fuel Polishing | Each system | On control panel | Fuel polishing is the removal of water, sediment and microbial contamination from fuels |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Supplemental Elements | G3060 | n/a | G3060 - Fuel Distribution - [Supplemental Elements] Fuel Polishing System | G3060 - Fuel Distribution | [Supplemental Elements] Fuel Polishing System |  | G. Fuel Distribution - [Supplemental Elements] Fuel Polishing System | G. Fuel Distribution | [Supplemental Elements] Fuel Polishing System |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
System | G3060.10 | Not on One-Line | G3060.10 - Fuel Distribution - Gas - (System) Natural Gas/Propane Fuel | G3060.10 - Fuel Distribution - Gas | (System) Natural Gas/Propane Fuel |  | G. Fuel Distribution - Natural/Propane Gas - (System) Natural Gas/Propane Fuel | G. Fuel Distribution - Natural/Propane Gas | (System) Natural Gas/Propane Fuel |  | SYS Natural Gas/Propane ([Area Served]) | Each system | No barcode - Track by location | The complete assets and components outside and inside the building that handle Natural Gas, LnG, propane purposes of space heating/cooling, cooking, emergency power, vehicle fueling, or lab use. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | G3060.10 | G30-1 | G3060.10 - Fuel Distribution - Gas - Stationary Propane Tank | G3060.10 - Fuel Distribution - Gas | Stationary Propane Tank |  | G. Fuel Distribution - Natural/Propane Gas - Stationary Propane Tank | G. Fuel Distribution - Natural/Propane Gas | Stationary Propane Tank |  | Stationary Propane Tank | Each pump set | On control panel | A stationary pressure vessel designed to store propane. |  | 21-04 30 10 30 | Fuel Pumps | 22-23 12 13 | Facility Fuel-Oil Pumps | 23-27 17 00 | Pumps
Supplemental Elements | G3060.10.99 | n/a | G3060.10 - Fuel Distribution - Gas - [Supplemental Elements] Natural Gas/Propane Fuel | G3060.10 - Fuel Distribution - Gas | [Supplemental Elements] Natural Gas/Propane Fuel |  | G. Fuel Distribution - Propane Gas - [Supplemental Elements] Natural Gas/Propane Fuel | G. Fuel Distribution - Propane Gas | [Supplemental Elements] Natural Gas/Propane Fuel |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
System | G3060.20 | G30-1 | G3060.20 - Fuel Distribution - Fuel Oil - (System) Fuel Oil | G3060.20 - Fuel Distribution - Fuel Oil | (System) Fuel Oil |  | G. Fuel Distribution - Fuel Oil - (System) Fuel Oil | G. Fuel Distribution - Fuel Oil | (System) Fuel Oil |  | SYS Fuel Oil ([Area Served]) | Each system | No barcode - Track by location | The complete assets and components outside and inside the building that store and handle fuel oil mainly for heating. May also supply in some cases emergency generators. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | G3060.20 | G30-1 | G3060.20 - Fuel Distribution - Fuel Oil - Fuel Oil Pump | G3060.20 - Fuel Distribution - Fuel Oil | Fuel Oil Pump |  | G. Fuel Distribution - Fuel Oil - Fuel Oil Pump | G. Fuel Distribution - Fuel Oil | Fuel Oil Pump |  | Fuel Oil Pump | Each pump set | On control panel | Pumps used to transfer fuel oil from storage to fuel burning equipment; typically hot water or steam boilers. |  | 21-04 30 10 30 | Fuel Pumps | 22-23 12 13 | Facility Fuel-Oil Pumps | 23-27 17 00 | Pumps
Asset | G3060.20 | G30-1 | G3060.20 - Fuel Distribution - Fuel Oil - Fuel Oil Tank - Above Ground | G3060.20 - Fuel Distribution - Fuel Oil | Fuel Oil Tank | Above Ground | G. Fuel Distribution - Fuel Oil - Fuel Oil Tank - Above Ground | G. Fuel Distribution - Fuel Oil | Fuel Oil Tank | Above Ground | Fuel Oil Tank - Above Ground | Each tank | Next to level gate, or no barcode and tracked by location | Above ground storage tank for fuel oil. Includes containment structure when so equipped. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 00 | Facility Fuel-Storage Tanks | 23-27 29 19 | Tanks
Asset | G3060.20 | G30-1 | G3060.20 - Fuel Distribution - Fuel Oil - Fuel Oil Tank - Type to be specified | G3060.20 - Fuel Distribution - Fuel Oil | Fuel Oil Tank | Type to be specified | G. Fuel Distribution - Fuel Oil - Fuel Oil Tank - Type to be specified | G. Fuel Distribution - Fuel Oil | Fuel Oil Tank | Type to be specified | Fuel Oil Tank - [Above Ground or Underground] | Each tank | Next to level gate, or no barcode and tracked by location | Storage tank for fuel oil. Includes containment structure when so equipped. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 00 | Facility Fuel-Storage Tanks | 23-27 29 19 | Tanks
Asset | G3060.20 | G30-1 | G3060.20 - Fuel Distribution - Fuel Oil - Fuel Oil Tank - Underground | G3060.20 - Fuel Distribution - Fuel Oil | Fuel Oil Tank | Underground | G. Fuel Distribution - Fuel Oil - Fuel Oil Tank - Underground | G. Fuel Distribution - Fuel Oil | Fuel Oil Tank | Underground | Fuel Oil Tank - Underground | Each tank | Next to level gate, or no barcode and tracked by location | Underground storage tanks for fuel oil. Includes containment structure when so equipped. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 00 | Facility Fuel-Storage Tanks | 23-27 29 19 | Tanks
Supplemental Elements | G3060.20.99 | n/a | G3060.20 - Fuel Distribution - Fuel Oil - [Supplemental Elements] Fuel Oil | G3060.20 - Fuel Distribution - Fuel Oil | [Supplemental Elements] Fuel Oil |  | G. Fuel Distribution - Fuel Oil - [Supplemental Elements] Fuel Oil | G. Fuel Distribution - Fuel Oil | [Supplemental Elements] Fuel Oil |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
System | G3060.30 | G30-1 | G3060.30 - Fuel Distribution - Gasoline - (System) Gasoline | G3060.30 - Fuel Distribution - Gasoline | (System) Gasoline |  | G. Fuel Distribution - Gasoline - (System) Gasoline | G. Fuel Distribution - Gasoline | (System) Gasoline |  | SYS Gasoline ([Area Served]) | Each system | No barcode - Track by location | The complete assets and components that store and handle gasoline for refueling vehicles and gas engine driven equipment. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | G3060.30 | G30-1 | G3060.30 - Fuel Distribution - Gasoline - Gasoline Pump | G3060.30 - Fuel Distribution - Gasoline | Gasoline Pump |  | G. Fuel Distribution - Gasoline - Gasoline Pump | G. Fuel Distribution - Gasoline | Gasoline Pump |  | Gasoline Pump | Each pump set | On control panel | Pumps used to transfer gasoline from storage tanks to either vehicles or containers specially designed to hold fuel. |  | 21-04 30 10 30 | Fuel Pumps | 22-23 12 16 | Facility Gasoline Dispensing Pumps | 23-27 17 00 | Pumps
Asset | G3060.30 | G30-1 | G3060.30 - Fuel Distribution - Gasoline - Gasoline Tank - Above Ground | G3060.30 - Fuel Distribution - Gasoline | Gasoline Tank | Above Ground | G. Fuel Distribution - Gasoline - Gasoline Tank - Above Ground | G. Fuel Distribution - Gasoline | Gasoline Tank | Above Ground | Gasoline Tank - Above Ground | Each tank | Next to level gate, or no barcode and tracked by location | A vented tank of steel or composite material and located above ground. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 23 | Facility Aboveground Fuel-Oil, Storage Tanks | 23-27 29 21 11 | Aboveground Tank Containments
Asset | G3060.30 | G30-1 | G3060.30 - Fuel Distribution - Gasoline - Gasoline Tank - Type to be specified | G3060.30 - Fuel Distribution - Gasoline | Gasoline Tank | Type to be specified | G. Fuel Distribution - Gasoline - Gasoline Tank - Type to be specified | G. Fuel Distribution - Gasoline | Gasoline Tank | Type to be specified | Gasoline Tank - [Above Ground or Underground] | Each tank | Next to level gate, or no barcode and tracked by location | A vented tank of steel or composite material. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 23 | Facility Aboveground Fuel-Oil, Storage Tanks | 23-27 29 21 11 | Aboveground Tank Containments
Asset | G3060.30 | G30-1 | G3060.30 - Fuel Distribution - Gasoline - Gasoline Tank - Underground | G3060.30 - Fuel Distribution - Gasoline | Gasoline Tank | Underground | G. Fuel Distribution - Gasoline - Gasoline Tank - Underground | G. Fuel Distribution - Gasoline | Gasoline Tank | Underground | Gasoline Tank - Underground | Each tank | Next to level gate, or no barcode and tracked by location | A vented tank of steel or composite material and located below ground. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 23 | Facility Aboveground Fuel-Oil, Storage Tanks | 23-27 29 21 11 | Aboveground Tank Containments
Supplemental Elements | G3060.30.99 | n/a | G3060.30 - Fuel Distribution - Gasoline - [Supplemental Elements] Gasoline | G3060.30 - Fuel Distribution - Gasoline | [Supplemental Elements] Gasoline |  | G. Fuel Distribution - Gasoline - [Supplemental Elements] Gasoline | G. Fuel Distribution - Gasoline | [Supplemental Elements] Gasoline |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
System | G3060.40 | G30-1 | G3060.30 - Fuel Distribution - Diesel - (System) Diesel | G3060.30 - Fuel Distribution - Diesel | (System) Diesel |  | G. Fuel Distribution - Diesel - (System) Diesel | G. Fuel Distribution - Diesel | (System) Diesel |  | SYS Diesel ([Area Served]) | Each system | No barcode - Track by location | The complete assets and components that store and handle diesel fuel for refueling vehicles and supporting emergency generators. |  | 21-04 20 60 50 | Processed Water Systems | 22-22 67 19 19 | Deionized-Water Equipment | 23-27 55 00 | Liquid Treatment Components
Asset | G3060.40 | G30-1 | G3060.30 - Fuel Distribution - Diesel - Belly Tank | G3060.30 - Fuel Distribution - Diesel | Belly Tank |  | G. Fuel Distribution - Diesel - Belly Tank | G. Fuel Distribution - Diesel | Belly Tank |  | Belly Tank | Each tank | At point of fill via chain and tag around fill pipe or attached to adjacent surface if not subject to contact with fuel. | Diesel Tank used to supply an emergency power generator. Belly Tanks are integral part of the generator base. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 13 33 | Fuel-Oil Storage Tank Pumps | 23-27 29 19 | Tanks
Asset | G3060.40 | Not on One-Line | G3060.30 - Fuel Distribution - Diesel - Day Tank | G3060.30 - Fuel Distribution - Diesel | Day Tank |  | G. Fuel Distribution - Diesel - Day Tank | G. Fuel Distribution - Diesel | Day Tank |  | Day Tank | Each tank | Next to level gate, or no barcode and tracked by location | Diesel Tank used to supply an emergency power generator. Day Tanks are generally located next to the generator.
Asset | G3060.40 | G30-1 | G3060.30 - Fuel Distribution - Diesel - Diesel Pump | G3060.30 - Fuel Distribution - Diesel | Diesel Pump |  | G. Fuel Distribution - Diesel - Diesel Pump | G. Fuel Distribution - Diesel | Diesel Pump |  | Diesel Pump | Each pump set | On control panel | Pumps used to transfer diesel from storage to day tank or to fueling station. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 13 33 | Fuel-Oil Storage Tank Pumps | 23-27 29 19 | Tanks
Asset | G3060.40 | G30-1 | G3060.30 - Fuel Distribution - Diesel - Diesel Tank - Above Ground | G3060.30 - Fuel Distribution - Diesel | Diesel Tank | Above Ground | G. Fuel Distribution - Diesel - Diesel Tank - Above Ground | G. Fuel Distribution - Diesel | Diesel Tank | Above Ground | Diesel Tank - Above Ground | Each tank | Next to level gate, or no barcode and tracked by location | A vented tank of steel or composite material and located at ground level. Smaller ones typically have integral secondary containment. May be horizontal or vertical. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 23 | Facility Aboveground Fuel-Oil, Storage Tanks | 23-27 29 21 11 | Aboveground Tank Containments
Asset | G3060.40 | G30-1 | G3060.30 - Fuel Distribution - Diesel - Diesel Tank - Type to be specified | G3060.30 - Fuel Distribution - Diesel | Diesel Tank | Type to be specified | G. Fuel Distribution - Diesel - Diesel Tank - Type to be specified | G. Fuel Distribution - Diesel | Diesel Tank | Type to be specified | Diesel Tank - [Above Ground or Underground] | Each tank | Next to level gate, or no barcode and tracked by location | A vented tank of steel or composite material. Smaller ones typically have integral secondary containment. May be horizontal or vertical. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 23 | Facility Aboveground Fuel-Oil, Storage Tanks | 23-27 29 21 11 | Aboveground Tank Containments
Asset | G3060.40 | G30-1 | G3060.30 - Fuel Distribution - Diesel - Diesel Tank - Underground | G3060.30 - Fuel Distribution - Diesel | Diesel Tank | Underground | G. Fuel Distribution - Diesel - Diesel Tank - Underground | G. Fuel Distribution - Diesel | Diesel Tank | Underground | Diesel Tank - Underground | Each tank | Next to level gate, or no barcode and tracked by location | A vented tank of steel or composite material and located at ground level. Smaller ones typically have integral secondary containment. May be horizontal or vertical. |  | 21-04 30 10 50 | Fuel Storage Tanks | 22-23 13 23 | Facility Aboveground Fuel-Oil, Storage Tanks | 23-27 29 21 11 | Aboveground Tank Containments
Supplemental Elements | G3060.40.99 | n/a | G3060.30 - Fuel Distribution - Diesel - [Supplemental Elements] Diesel | G3060.30 - Fuel Distribution - Diesel | [Supplemental Elements] Diesel |  | G. Fuel Distribution - Diesel - [Supplemental Elements] Diesel | G. Fuel Distribution - Diesel | [Supplemental Elements] Diesel |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | G4010 |  | G4010 - Site Utilities - Groundings | G4010 - Site Utilities - Groundings |  |  | G. Site - Groundings | G. Site - Groundings | [5 empty] | General Category |  |  |  | 22-33 79 00 | Site Grounding | 23-35 39 11 | Electrical Grounding Device
System | G4010 | Not on One-Line | G4010 - Site Utilities - Groundings - (System) Groundings / Lighting Protection | G4010 - Site Utilities - Groundings | (System) Groundings / Lighting Protection |  | G. Site - Groundings - (System) Groundings / Lighting Protection | G. Site - Groundings | (System) Groundings / Lighting Protection |  | SYS Lighting Protection ([Area Served]) | As needed | Tracked by location | A dedicated system that consists of metal rods located at high points of a structure connected to substantial cable and terminating in rods or grids buried in the earth. A lightening strike is absorbed by the system safely moving the energy to the ground and protecting the structure. |  | 21-07 40 10 70 | Site Grounding | 22-33 79 93 | Site Lightning Protection | 23-35 39 15 | Lightning Protection
Supplemental Elements | G4010.99 | n/a | G4010 - Site Utilities - Groundings - [Supplemental Elements] Groundings / Lighting Protection | G4010 - Site Utilities - Groundings | [Supplemental Elements] Groundings / Lighting Protection |  | G. Site - Groundings - [Supplemental Elements] Groundings / Lighting Protection | G. Site - Groundings | [Supplemental Elements] Groundings / Lighting Protection |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | G4050 |  | G4050 - Site Lighting | G4050 - Site Lighting |  |  | G. Site - Lighting | G. Site - Lighting | [5 empty] | General Category |  | 21-07 40 50 | Site Lighting | 22-26 56 00 | Exterior Lighting
System | G4050 | Not on One-Line | G4050 - Site Lighting - (System) Site Lighting | G4050 - Site Lighting | (System) Site Lighting |  | G. Site - Lighting - (System) Site Lighting | G. Site - Lighting | (System) Site Lighting |  | SYS Sight Lighting ([Area Served]) | As needed | Tracked by location | Exterior Site lighting |  | 21-07 20 80 70 | Landscape Lighting | 22-26 56 23 | Area Lighting
Asset | G4050 | Not on One-Line | G4050 - Site Lighting - Area Lighting | G4050 - Site Lighting | Area Lighting |  | G. Site - Lighting - Area Lighting | G. Site - Lighting | Area Lighting |  | Area Lighting | As needed | Tracked by location | General lighting source for walkways and parking lots. |  | 21-07 20 80 70 | Landscape Lighting | 22-26 56 23 | Area Lighting
Asset | G4050 | Not on One-Line | G4050 - Site Lighting - Flood Lighting | G4050 - Site Lighting | Flood Lighting |  | G. Site - Lighting - Flood Lighting | G. Site - Lighting | Flood Lighting |  | Flood Lighting | As needed | Tracked by location | High intensity lighting to illuminate a large area. |  | 21-07 20 80 70 | Landscape Lighting | 22-26 56 26 | Flood Lighting
Asset | G4050 | Not on One-Line | G4050 - Site Lighting - Roadway Lighting | G4050 - Site Lighting | Roadway Lighting |  | G. Site - Lighting - Roadway Lighting | G. Site - Lighting | Roadway Lighting |  | Roadway Lighting | As needed | Tracked by location | Lighting typically mounted on poles to lights up any owner roads at night for safe driving. |  | 21-07 20 80 70 | Landscape Lighting | 22-26 56 26 | Roadway Lighting
Supplemental Elements | G4050.99 | n/a | G4050 - Site Lighting - [Supplemental Elements] Site Lighting | G4050 - Site Lighting | [Supplemental Elements] Site Lighting |  | G. Site - Lighting - [Supplemental Elements] Site Lighting | G. Site - Lighting | [Supplemental Elements] Site Lighting |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification
Grouping | Z1020 |  | Z1020 - Admin Procedures | Z1020 - Admin Procedures |  |  | Z. Admin Procedures | Z. Admin Procedures | [5 empty] | General Category
Admin | Z1020 | Not on One-Line | Z1020 - Admin Procedures - Air Emission Data Reporting - Boiler | Z1020 - Admin Procedures | Air Emission Data Reporting | Boiler | Z. Admin Procedures - Air Emission Data Reporting - Boiler | Z. Admin Procedures | Air Emission Data Reporting | Boiler | Boiler | n/a | n/a | This is a general category for air emission reporting
Admin | Z1020 | Not on One-Line | Z1020 - Admin Procedures - Air Emission Data Reporting - Generator | Z1020 - Admin Procedures | Air Emission Data Reporting | Generator | Z. Admin Procedures - Air Emission Data Reporting - Generator | Z. Admin Procedures | Air Emission Data Reporting | Generator | Generator | n/a | n/a | This is a general category for air emission reporting
Admin | Z1020 | Not on One-Line | Z1020 - Admin Procedures - Fire Drill | Z1020 - Admin Procedures | Fire Drill |  | Z. Admin Procedures - Fire Drill | Z. Admin Procedures | Fire Drill |  | Fire Drill | n/a | n/a | This is a general category for scheduling AHJ mandated fire drills |  | n/a | n/a | 22-01 30 00 | Administrative Requirements
Admin | Z1020 | Not on One-Line | Z1020 - Admin Procedures - PPE Inspection | Z1020 - Admin Procedures | PPE Inspection |  | Z. Admin Procedures - PPE Inspection | Z. Admin Procedures | PPE Inspection |  | PPE Inspection | n/a | n/a | This is a general category for scheduling PPE Inspections
Admin | Z1020 | Not on One-Line | Z1020 - Admin Procedures - Quarterly Aggregate ILSM Assessment | Z1020 - Admin Procedures | Quarterly Aggregate ILSM Assessment |  | Z. Admin Procedures - Quarterly Aggregate ILSM Assessment | Z. Admin Procedures | Quarterly Aggregate ILSM Assessment |  | Quarterly Aggregate ILSM Assessment | n/a | n/a | This is a general category for scheduling quarterly, aggregate ILSM Inspections |  | n/a | n/a | 22-01 30 00 | Administrative Requirements
Admin | Z1020 | Not on One-Line | Z1020 - Admin Procedures - Water Safety Testing | Z1020 - Admin Procedures | Water Safety Testing |  | Z. Admin Procedures - Water Safety Testing | Z. Admin Procedures | Water Safety Testing |  | Water Safety Testing | n/a | n/a | This is a general category for water safety testing reporting
Supplemental Elements | Z1020.99 | n/a | Z1020 - Admin Procedures - [Supplemental Elements] Admin Procedures | Z1020 - Admin Procedures | [Supplemental Elements] Admin Procedures |  | Z. Admin Procedures - [Supplemental Elements] Admin Procedures | Z. Admin Procedures | [Supplemental Elements] Admin Procedures |  |  | As needed | As needed | This category is used for assets not identified elsewhere in this classification

## 6) Diagrams
Data Standardization in Health Care Facility Management
Diagrammatic Representation of Building Systems and Assets
Version 0.9
The ASHE Operational Excellence Committee is currently working on a diagrammatic representation of building systems and assets
to provide the context needed to set up meaningful and effective asset registers.
Contact Charlie Palmer (cpalmer@enstoa.com) if you want to join the working group.
The following drawings are expected to be published by the Operational Excellence Committee:
C10-1 Egress and Barrier Walls
D10-1 Pneumatic Tube System
D10-2 Chutes
D20-1 Domestic Water
D20-2 Lab Air
D20-3 Medical Air
D20-4 Medical-Lab Vacuum
D20-5 WAGD Vacuum
D20-6 Medical Gas Oxygen
D20-7 Medical Gas Nitrogen
D20-8 Medical Gas Nitrous Oxide
D20-9 Medical Gas Carbon Dioxide | Example:
D30-1 Steam Heating and Distribution | D30-1 Steam Heating and Distribution
D30-2 Hydronic Central Heating
D30-3 DX Cooling
D30-3 Hydronic Central Cooling
D30-3b Air Cooled Chiller
D30-5 HVAC Air Handling
D40-1a Fire Risers
D40-1b Fire Pumps
D40-1c House Tanks
D50-1 Electrical Power Generation
D50-1 Electrical Service and Distribution
D50-3 Emergency Lighting
D70-1 Fire Detection and Alarm
G-10 Site Fuel Distribution
Example:
D40-1a Fire Risers
Example:
D40-1b Fire Pumps